## Loads
CUY-14 Utility Bridge: Conceptual Design |  |  |  | Calculated: | MDP | 2022-11-18
Design Loads (Revised, 7/7/2023) |  |  |  | Checked: | ARA | 2022-11-28
|  |  |  | Revised: | MDP | 2023-07-07
15" Sanitary Line:
Pipe and Water Weight:
| Pipe Inside Diameter = | 15 | inches | Pipe Outer Area = | 201.0619 | in2
| Pipe Thickness = | 0.5 | inches | Pipe Inner Area = | 176.7146 | in2
| Pipe Unit Weight = | 490 | lb/ft3 | Pipe Weight = | 82.8486 | lbs/ft
| Water Unit Weight = | 62.4 | lb/ft3 | Water Weight = | 76.5763 | lbs/ft
Utility Rack Weight:
| Avg. Roller Diameter = | 3 | inches | Roller Weight = | 8.4185 | lbs/ft
| Roller Length = | 1.75 | feet | Hanger Weight = | 1.3363 | lbs/ft
| No. of Rollers = | 2 |  | Contingency = | 1.951 | lbs/ft
| Hanger Diameter = | 1 | inches
| Hanger Length = | 2.5 | feet
| No. of Hangers = | 2
| Rack/Diaphragm Spacing = | 10 | feet | 15" Sanitary Weight = | 180 | lbs/ft
| Rack Unit Weight = | 490 | lb/ft3
| Weight Contingency = | 20%
8" Gas Line with Powercrete Coating (Per Gas Line):
Pipe Weight:
| Pipe Inside Diameter = | 8 | inches | Pipe Outer Area = | 63.6173 | in2
| Pipe Thickness = | 0.5 | inches | Pipe Inner Area = | 50.2655 | in2
| Pipe Unit Weight = | 490 | lb/ft3 | Powercrete Outer Area = | 113.0973 | in2
| Powercrete Thickness = | 1.5 | inches | Pipe Weight = | 45.4331 | lbs/ft
| Powercrete Unit Weight = | 150 | lb/ft3 | Powercrete Weight = | 51.5418 | lbs/ft
Utility Rack Weight:
| Avg. Roller Diameter = | 2 | inches | Roller Weight = | 2.138 | lbs/ft
| Roller Length = | 1 | feet | Hanger Weight = | 0.80176 | lbs/ft
| No. of Rollers = | 2 |  | Contingency = | 0.58796 | lbs/ft
| Hanger Diameter = | 1 | inches
| Hanger Length = | 1.5 | feet
| No. of Hangers = | 2
| Rack/Diaphragm Spacing = | 10 | feet | 8" Gas Weight = | 110 | lbs/ft, each
| Rack Unit Weight = | 490 | lb/ft3
| Weight Contingency = | 20%
AT&T Duct Bank of NineTwelve, 5" Conduits:
| Conduit Weight = | 1.5 | lbs/ft | Conduit & Cable Weight = | 198 | lbs/ft
| No. of Conduits = | 12 |  | Rack Weight = | 1.5 | lbs/ft
| Cable Weight = | 15 | lbs/ft | Contingency = | 49.875 | lbs/ft
| Rack Weight = | 15 | pounds
| Rack/Diaphragm Spacing = | 10 | feet
| Weight Contingency = | 25% |  | AT&T Duct Bank Weight = | 250 | lbs/ft
CEI Line of Nine, 5" Conduits:
| Conduit Weight = | 1.5 | lbs/ft | Conduit & Cable Weight = | 148.5 | lbs/ft
| No. of Conduits = | 9 |  | Contingency = | 14.85 | lbs/ft
| Cable Weight = | 15 | lbs/ft
| Weight Contingency = | 10%
|  |  |  | CEI Duct Weight = | 170 | lbs/ft
Live Load on Inspection Walkway: | [5 empty] | ASCE-7, Table 4.3-1
| Uniform Lo = | 40 | lb/ft2
| Uniform Lo Width = | 2 | feet
| Concentrated LL = | 300 | lbs | Live Load Weight = | 80 | lbs/ft
| Diaphragm Spacing = | 10 | feet