## Circuit EX-51
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | PS-5 | Circuit: | EX - 51 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'EX-51' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
5117 | 5116 | 315 | 0.8 | 0.8 | 252 | 4 | 0.15624 | 0.15624 | 0.03255 | 5117
5116 | 5115 | 245 | 0.8 | 1.6 | 392 | 4 | 0.24304 | 0.39928 | 0.083183 | 5116
5115 | 5114 | 240 | 0.8 | 2.4 | 576 | 4 | 0.35712 | 0.7564 | 0.15758 | 5115
5114 | 5113 | 255 | 0.8 | 3.2 | 816 | 4 | 0.50592 | 1.2623 | 0.26298 | 5113
5113 | 5112 | 263 | 0.8 | 4 | 1052 | 4 | 0.65224 | 1.9146 | 0.39887 | 5112
5112 | 5111 | 264 | 0.8 | 4.8 | 1267.2 | 4 | 0.78566 | 2.7002 | 0.56255 | 5111
5111 | 5110 | 244 | 1.9 | 6.7 | 1634.8 | 4 | 1.0136 | 3.7138 | 0.77371 | 5110
5110 | 5109 | 244 | 1.9 | 8.6 | 2098.4 | 4 | 1.301 | 5.0148 | 1.0448 | 5109
5109 | 5108 | 234 | 1.9 | 10.5 | 2457 | 4 | 1.5233 | 6.5381 | 1.3621 | 5108
5108 | 5107 | 254 | 1.9 | 12.4 | 3149.6 | 4 | 1.9528 | 8.4909 | 1.7689 | 5107
5107 | 5106 | 235 | 1.9 | 14.3 | 3360.5 | 4 | 2.0835 | 10.5744 | 2.203 | 5106
5106 | 5105 | 235 | 1.9 | 16.2 | 3807 | 4 | 2.3603 | 12.9348 | 2.6947 | 5105
5105 | 5104 | 235 | 1.9 | 18.1 | 4253.5 | 4 | 2.6372 | 15.5719 | 3.2441 | 5104
5104 | 5103 | 225 | 1.9 | 20 | 4500 | 4 | 2.79 | 18.3619 | 3.8254 | 5103
5103 | 5102 | 225 | 1.9 | 21.9 | 4927.5 | 4 | 3.055 | 21.417 | 4.4619 | 5102
5102 | 5101 | 225 | 1.9 | 23.8 | 5355 | 4 | 3.3201 | 24.7371 | 5.1536 | 5101
5101 | PS-5 | 65 | 1.9 | 25.7 | 1670.5 | 4 | 1.0357 | 25.7728 | 5.3693 | PS-5
FOR LUMINAIRE 5112 to 5117 ASSUME USE OF GE ERL2021B330AGRAYL; 174 WATTS; 20,300 INITIAL LAMP LUMENS
174 WATTS / 480 VOLTS = .3625 AMPS = 0.4 AMPS
0.4 AMPS X 2 LIGHTS PER POLE = 0.8 AMPS
120
240
480