## (E) PANEL C
P A N E L B O A R D S C H E D U L E | [20 empty] | WIRE SPECS |  |  | WIRECHECK |  | CONN/DEMAND CELL LINK | 0
(E) PANEL C |  | VOLTS: |  | 240 | MAINS RATING: |  |  | A.I.C. RATING: | [5 empty] | LOCATION: |  | SHOP |  |  |  |  | AMPERAGE | WIRESIZE | IMPEDANCE | WIRESIZE | AMPERAGE | WIRE TYPE CELL LINK | 0
|  | PHASE: |  | 1 | MCB: | 100A |  | BRKR SPACE: |  |  | 20 |  |  | SOURCE: |  | UTILITY |  |  |  |  | 0 | 12 | 1.7 | 12 | 20
|  | WIRE: |  | 3 | MLO: |  |  | MTG./NEMA #: |  |  | NEMA 1 |  |  | FEEDER: |  | 3#2, 1#8GND, 1 1/4" CND |  |  |  |  | 20 | 10 | 1.1 | 10 | 30
| LOAD | LOAD VOLT-AMPERES | [11 empty] | LOAD VOLT-AMPERES |  |  |  |  | LOAD |  | 85 | 3 | 0.24 | 3 | 100
CKT | DESCRIPTION | LTS | REC | MOTOR | OTHER | KIT | OCPD | P | CKT | PH | CKT | P | OCPD | LTS | REC | MOTOR | OTHER | KIT | DESCRIPTION | CKT | 100 | 2 | 0.2 | 2 | 115
1 | (E) WELDER | LOAD VOLT-AMPERES OTHER: 1400; LOAD VOLT-AMPERES OCPD: 30; LOAD VOLT-AMPERES P: 2; LOAD VOLT-AMPERES CKT: 1; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 2; LOAD VOLT-AMPERES P: 2; LOAD VOLT-AMPERES OCPD: 30; LOAD VOLT-AMPERES OTHER: 1200 | (E) AIR | 2 | 115 | 1 | 0.16 | 1 | 130
3 |  | LOAD VOLT-AMPERES OTHER: 1400; LOAD VOLT-AMPERES CKT: 3; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 4; LOAD VOLT-AMPERES OTHER: 1200 |  | 4 | 130 | 1/0 | 0.13 | 1/0 | 150
5 | EXISTING LOAD | LOAD VOLT-AMPERES REC: 720; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 5; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 6; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES REC: 720 | (E) WEST WALL RECEPTS | 6 | 150 | 2/0 | 0.11 | 2/0 | 175
7 | (E) SNAP-ON | LOAD VOLT-AMPERES OTHER: 600; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 2; LOAD VOLT-AMPERES CKT: 7; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 8; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES REC: 720 | (E) FRONT WALL RECEPTS | 8 | 175 | 3/0 | 0.094 | 3/0 | 200
9 |  | LOAD VOLT-AMPERES OTHER: 600; LOAD VOLT-AMPERES CKT: 9; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 10; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES LTS: 750 | (E) FRONT LIGHT | 10 | 200 | 4/0 | 0.08 | 4/0 | 230
11 | (E) WEST WALL RECEPTS | LOAD VOLT-AMPERES REC: 720; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 11; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 12; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES LTS: 750 | (E) BACK LIGHT | 12 | 230 | 250 | 0.073 | 250 | 255
13 | (E) REF | LOAD VOLT-AMPERES OTHER: 1000; LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 13; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 14; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | SPARE | 14 | 255 | 300 | 0.065 | 300 | 285
15 | (E) EXISTING LOAD | LOAD VOLT-AMPERES OTHER: 1000; LOAD VOLT-AMPERES OCPD: 30; LOAD VOLT-AMPERES P: 2; LOAD VOLT-AMPERES CKT: 15; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 16; LOAD VOLT-AMPERES P: 1 | SPACE | 16 | 285 | 350 | 0.06 | 350 | 310
17 |  | LOAD VOLT-AMPERES OTHER: 1000; LOAD VOLT-AMPERES CKT: 17; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 18; LOAD VOLT-AMPERES P: 1 | SPACE | 18 | 310 | 400 | 0.056 | 400 | 335
19 | SPACE | LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 19; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 20; LOAD VOLT-AMPERES P: 1 | SPACE | 20 | 335 | 500 | 0.05 | 500 | 380
21 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 21; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 22; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 22 | 380 | 600 | 0.047 | 600 | 420
23 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 23; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 24; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 24 | 420 | (2) 4/0 | 0.045 | (2) 4/0 | 460
25 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 25; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 26; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 26 | 460 | (2) 250 | 0.04 | (2) 250 | 510
27 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 27; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 28; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 28 | 510 | (2) 300 | 0.04 | (2) 300 | 570
29 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 29; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 30; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 30 | 570 | (2) 350 | 0.04 | (2) 350 | 620
31 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 31; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 32; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 32 | 620 | (2) 400 | 0.04 | (2) 400 | 670
33 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 33; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 34; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 34 | 670 | (2) 500 | 0.04 | (2) 500 | 760
35 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 35; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 36; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 36 | 760 | (2) 600 | 0.04 | (2) 600 | 840
37 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 37; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 38; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 38 | 840 | VERIFY | VERIFY | VERIFY
39 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 39; LOAD VOLT-AMPERES PH: B; LOAD VOLT-AMPERES CKT: 40; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 40
41 | NOT USEABLE | LOAD VOLT-AMPERES OCPD: 20; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES CKT: 41; LOAD VOLT-AMPERES PH: A; LOAD VOLT-AMPERES CKT: 42; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 20 | NOT USEABLE | 42
| SUBTOTAL CONNECTED KVA | LOAD VOLT-AMPERES PH: LOAD SUMMARY & FEEDER CALCULATION
|  | LTS | REC | MOTOR | OTHER | KIT | TOTAL |  |  | LTS |  | REC | MOTOR | OTHER | KIT | SUBTOT | SPARE | TOTAL
| PHASE A CONNECTED KVA | 0.75 | 1.44 | 0 | 5.2 | 0 | 7.39 |  |  | 1.5 |  | 2.88 | 0 | 9.4 | 0 | 13.78 | 25% |  | CONNECTED KVA
| PHASE B CONNECTED KVA | 0.75 | 1.44 | 0 | 4.2 | 0 | 6.39 |  |  | 1.0 |  | #1 | 1 | 1 | 1 |  |  |  | DEMAND FACTOR
| 25% OF LARGEST MOTOR | LOAD VOLT-AMPERES MOTOR: 0; LOAD VOLT-AMPERES OCPD: 0; LOAD VOLT-AMPERES PH: 1.5; LOAD VOLT-AMPERES P: 2.88; LOAD VOLT-AMPERES OCPD: 0; LOAD VOLT-AMPERES LTS: 9.4; LOAD VOLT-AMPERES REC: 0; LOAD VOLT-AMPERES MOTOR: 13.78; LOAD VOLT-AMPERES OTHER: 3.445; LOAD VOLT-AMPERES KIT: 17.225 | DEMAND KVA
|  | LOAD VOLT-AMPERES KIT: 71.7708 | DEMAND AMPS
|  | LOAD VOLT-AMPERES PH: 1.25; LOAD VOLT-AMPERES P: 1; LOAD VOLT-AMPERES OCPD: 1; LOAD VOLT-AMPERES LTS: 1; LOAD VOLT-AMPERES REC: 1; LOAD VOLT-AMPERES OTHER: 1 | CONTINUOUS/NONCONT FACTOR
| RECEPTACLE DEMAND FACTOR: | LOAD VOLT-AMPERES KIT: 73.3333 | MIN. OVERCURRENT DEVICE AMPS
#1: 100% FIRST 10 KVA + 50% REMAINING
**NO NEW LOAD ON EXISTING PANEL**
Note on M32: INSERT #1 FOR NORMAL CODE DEMAND OR #2 FOR HOSPITAL DEMAND, SEE NOTE AT LEFT.

## DialogData (hidden)
Mounting Cell Link | 2
Type Cell Link | 1
Spaces Cell Link | 1
Voltage Cell Link | 2
Mains Cell Link | 2
Mains Amperage Cell Link | 5
AIC Cell Link | 1