## Sheet1
VOLTAGE DROP CALCULATIONS
HIGHWAY LIGHTING |  |  |  | NO. OF WIRES FOR CALCULATION PURPOSES: 2
SUPPLY VOLTAGE: 120/240V, 2 WIRE PLUS GROUND
NO. 6 AWG: 0.49 PER NEC CH. 9, TABLE 8
152W LED LINE AMPS = 0.63 |  |  |  | WIRE FACTOR USED: TWO NO. 6 AWG WIRES: |  |  |  | 0.98 | OHMS/MF/1000
SECTION |  |  | AMPERES |  | AMPERE- | WIRE | VOLTAGE DROP
FROM | TO | FEET | AT POINT | ACCUM. | FEET | AWG | IN SECTION | ACCUM. | % DROP | AT POINT
L-5 | L-6 | 156 | 0.63 | 0.63 | 98.28 | 6 | 0.096314 | 2.5283 | 1.0534 | L-5
L-6 | L-7 | 112 | 0.63 | 1.26 | 141.12 | 6 | 0.1383 | 2.4319 | 1.0133 | L-6
L-7 | L-8 | 107 | 0.63 | 1.89 | 202.23 | 6 | 0.19819 | 2.2936 | 0.95568 | L-7
L-8 | PB-2 | 82 | 0.63 | 2.52 | 206.64 | 6 | 0.20251 | 2.0955 | 0.87311 | L-8
L-9 | PB-2 | 90 | 0.63 | 0.63 | 56.7 | 6 | 0.055566 | 1.9485 | 0.81188 | L-9
PB-2 | PB-3 | 77 | 0 | 3.15 | 242.55 | 6 | 0.2377 | 1.8929 | 0.78873 | PB-2
PB-3 | L-10 | 18 | 0 | 3.15 | 56.7 | 6 | 0.055566 | 1.6552 | 0.68969 | PB-3
L-10 | L-11 | 76 | 0.63 | 3.78 | 287.28 | 6 | 0.28153 | 1.5997 | 0.66653 | L-10
L-11 | PB-4 | 78 | 0.63 | 4.41 | 343.98 | 6 | 0.3371 | 1.3181 | 0.54923 | L-11
PB-4 | PB-1 | 58 | 0 | 4.41 | 255.78 | 6 | 0.25066 | 0.98105 | 0.40877 | PB-4
PB-1 | L-12 | 17 | 0 | 4.41 | 74.97 | 6 | 0.073471 | 0.73038 | 0.30433 | PB-1
L-12 | PB-5 | 100 | 0.63 | 5.04 | 504 | 6 | 0.49392 | 0.65691 | 0.27371 | L-12
L-4 | L-3 | 132 | 0.63 | 0.63 | 83.16 | 6 | 0.081497 | 0.61431 | 0.25596 | L-4
L-3 | L-2 | 86 | 0.63 | 1.26 | 108.36 | 5 | 0.10619 | 0.53282 | 0.22201 | L-3
L-2 | L-1 | 109 | 0.63 | 1.89 | 206.01 | 6 | 0.20189 | 0.42662 | 0.17776 | L-2
L-1 | PB-5 | 25 | 0.63 | 2.52 | 63 | 6 | 0.06174 | 0.22473 | 0.093639 | L-1
PB-5 | LLC | 22 | 0 | 7.56 | 166.32 | 6 | 0.16299 | 0.16299 | 0.067914 | PB-5