## Circuit A
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | HEN-108-17.40 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 1 | 12 | 2
Power Service: |  | EX. | Circuit: | A |  |  |  | U-X | AMPS | 0.49833 | 10 | 1.2
Supply Voltage: |  | 120 | [5 empty] | A-X | AMPS | 0.60667 | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 |  | A-X | LUMINAIRE WATTAGE - 56 |  |  | 6 | 0.49
|  | No. | 6 | AWG. | 0.49 |  | U-X | LUMINAIRE WATTAGE - 46 |  |  | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 120 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'A' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
U-1 | PB A-8 | 10 | 0.49833 | 0.49833 | 4.9833 | 6 | 0.0048837 | 1.7034 | 1.4195 | U-1
PB A-8 | PB A-7 | 113 | 0 | 0.49833 | 56.3117 | 6 | 0.055185 | 1.6985 | 1.4154 | PB A-8
U-2 | PB A-7 | 10 | 0.49833 | 0.99667 | 9.9667 | 6 | 0.0097673 | 1.6433 | 1.3694 | U-2
PB A-7 | PB A-1 | 173 | 0 | 0.99667 | 172.4233 | 6 | 0.16897 | 1.6336 | 1.3613 | PB A-7
A1 | PB A-1 | 95.4 | 0.60667 | 1.6033 | 152.958 | 6 | 0.1499 | 1.4646 | 1.2205 | A1
PB A-1 | A2 | 41.2 | 0 | 1.6033 | 66.0573 | 6 | 0.064736 | 1.3147 | 1.0956 | PB A-1
A2 | A3 | 156.6 | 0.60667 | 2.21 | 346.086 | 6 | 0.33916 | 1.25 | 1.0416 | A2
A3 | PB A-2 | 46.4 | 0.60667 | 2.8167 | 130.6933 | 6 | 0.12808 | 0.91079 | 0.75899 | A3
PB A-2 | PB A-3 | 32 | 0.60667 | 3.4233 | 109.5467 | 6 | 0.10736 | 0.78271 | 0.65226 | PB A-2
PB A-3 | A-6 | 37.4 | 0.60667 | 4.03 | 150.722 | 6 | 0.14771 | 0.67536 | 0.5628 | PB A-3
A-6 | PB A-4 | 75.6 | 0.60667 | 4.6367 | 350.532 | 6 | 0.34352 | 0.52765 | 0.43971 | A-6
PB A-4 | PB A-6 | 13.3 | 2.4267 | 7.0633 | 93.9423 | 6 | 0.092063 | 0.18413 | 0.15344 | PB A-4
PB A-6 | CC | 13.3 | 0 | 7.0633 | 93.9423 | 6 | 0.092063 | 0.092063 | 0.07672 | PB A-6
A-4 | PB A-2 | 162 | 0.60667 | 0.60667 | 98.28 | 6 | 0.096314 | 0.096314 | 0.080262 | A-4
A-5 | PB A-3 | 44.3 | 0.60667 | 0.60667 | 26.8753 | 6 | 0.026338 | 0.026338 | 0.021948 | A-5
A-9 | A-8 | 90.1 | 0.60667 | 0.60667 | 54.6607 | 6 | 0.053567 | 0.17687 | 0.14739 | A-9
A-8 | PB A-5 | 31.7 | 0.60667 | 1.2133 | 38.4627 | 6 | 0.037693 | 0.12331 | 0.10276 | A-8
PB A-5 | PB A-4 | 48 | 0 | 1.82 | 87.36 | 6 | 0.085613 | 0.085613 | 0.071344 | PB A-5
A-7 | PB A-4 | 53.8 | 0.60667 | 0.60667 | 32.6387 | 6 | 0.031986 | 0.031986 | 0.026655 | A-7
120 | [5 empty] | 6
240 | [5 empty] | 6
480 | [5 empty] | 6
A-10 | PB A-5 | 157 | 0.60667 | 0.60667 | 95.2467 | 6 | 0.093342 | 0.093342 | 0.077785 | A-10