## WireFormula (hidden)
Wire Size | Ohms per 1000 ft @ 75C
18 | 7.95
16 | 4.99
14 | 3.14
12 | 1.98
10 | 1.24
8 | 0.778
6 | 0.491
4 | 0.308
3 | 0.245
2 | 0.194
1 | 0.154
1/0 | 0.122
2/0 | 0.0967
3/0 | 0.0766
4/0 | 0.0608

## Circuit A
LED VOLTAGE DROP CALCULATION
| LOCATION: | LIC-16-15.93 |  |  |  |  | CIRCUIT: | A
| PID: | 97990 |  |  |  |  | WIRE SIZE (AWG): | 8
| POWER SERVICE: | 1 |  |  |  |  | VOLTAGE: | 240
[7 empty] | BALLAST FACTOR: | 1
LED WATTAGE | FROM | TO | LENGTH (FEET) | AMPERES |  | VOLTAGE DROP
|  |  |  | AT POINT | ACCUM. | IN SECTION | ACCUM. | PERCENT (5% MAX.) | AT POINT
50 | A-1 | A-2 | 48 | 0.20833 | 0.20833 | 0.01556 | 0.67427 | 0.28094 | A-1
50 | A-2 | A-3 | 48 | 0.20833 | 0.41667 | 0.03112 | 0.65871 | 0.27446 | A-2
50 | A-3 | A-4 | 48 | 0.20833 | 0.625 | 0.04668 | 0.62759 | 0.26149 | A-3
50 | A-4 | A-5 | 48 | 0.20833 | 0.83333 | 0.06224 | 0.58091 | 0.24204 | A-4
50 | A-5 | PB-3 | 15 | 0.20833 | 1.0417 | 0.024313 | 0.51867 | 0.21611 | A-5
0 | PB-3 | PB-2 | 40 | 0 | 1.0417 | 0.064833 | 0.49435 | 0.20598 | PB-3
0 | PB-2 | PB-1 | 50 | 0 | 1.0417 | 0.081042 | 0.42952 | 0.17897 | PB-2
0 | PB-1 | PS-1 | 15 | 0 | 1.0417 | 0.024313 | 0.34848 | 0.1452 | PB-1
0 | PS-1 | TRANS | 200 | 0 | 1.0417 | 0.32417 | 0.32417 | 0.13507 | PS-1
|  | TOTAL LENGTH = | 512 | TOTAL CIRCUIT AMP = | 1.0417
[5 empty] | 0.25 | kVa

## Lighting Load Table
LIGHTING LOAD TABLE
CIRCUIT | LUMINAIRES | WATTS/ LUMINAIRE | TOTAL WATTS (BALLAST) | KVA | A (@ VOLTS) | CIRCUIT FUSE SIZE (MIN.) | CIRCUIT FUSE SIZE
A | 5 | 50 | 250 | 0.25 | 1.0417 | 1.3021 | 30

## Power Service Data
POWER SERVICE DATA
POWER SERVICE | LINE VOLTS | CONNECTED LOAD (KVA) | SERVICE ENTRANCE CONDUCTOR SIZE NO. (AWG) | ENCLOSURE RATING (AMPS) | CIRCUIT NO. | CIRCUIT LOAD (AMPS) | CIRCUIT FUSE SIZE (AMPS) | CIRCUIT CABLE SIZE (AWG) | MAINTAINING AGENCY
1 | 120/240V 1 PHASE 3-WIRE W/ NETRUAL GND. | 0.25 | 4 | 60 | A | 1.0417 | 30 | 4 & 10 | ODOT
[5 empty] | **B | 0 | 30 | N/A
**CIRCUIT FOR FUTURE USE