## Circuit X
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | MOT | 725 | 14.41 |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | EXISTING CC1 | Circuit: | [7 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 2 | AWG. | 0.19 | [5 empty] | 6 | 0.49
|  | No. | 4 | AWG. | 0.31 | [5 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
HL-6 | EPB-50 | 32 | 2.44 | 2.44 | 78.08 | 2 | 0.02967 | 0.02967 | 0.0061813 | HL-6
EPB-50 | EPB-51 | 534 | 0 | 2.44 | 1302.96 | 2 | 0.49512 | 0.5248 | 0.10933 | EPB-50
EPB-51 | EPB-52 | 68 | 0 | 2.44 | 165.92 | 2 | 0.06305 | 0.58784 | 0.12247 | EPB-51
EPB-52 | HL-7 | 9 | 3.66 | 6.1 | 54.9 | 2 | 0.020862 | 0.60871 | 0.12681 | EPB-52
EPB-52 | EPB-53 | 539 | 0 | 6.1 | 3287.9 | 2 | 1.2494 | 1.8581 | 0.38711 | EPB-52
EPB-53 | HL-8 | 37 | 3.66 | 9.76 | 361.12 | 2 | 0.13723 | 1.9953 | 0.41569 | EPB-53
EPB-53 | EPB-54 | 411 | 0 | 9.76 | 4011.36 | 2 | 1.5243 | 3.5197 | 0.73326 | EPB-53
EPB-54 | HL-9 | 34 | 3.66 | 13.42 | 456.28 | 2 | 0.17339 | 3.693 | 0.76938 | EPB-54
EPB-54 | PB-5 | 171 | 0 | 13.42 | 2294.82 | 2 | 0.87203 | 4.5651 | 0.95106 | EPB-54
HL-1 | EPB-55 | 49 | 3.66 | 3.66 | 179.34 | 4 | 0.11119 | 4.6763 | 0.97422 | HL-1
EPB-55 | PB-5 | 179 | 0 | 3.66 | 655.14 | 4 | 0.40619 | 5.0824 | 1.0588 | EPB-55
PB-5 | PB-6 | 66 | 0 | 18.3 | 1207.8 | 4 | 0.74884 | 5.8313 | 1.2149 | PB-5
PB-6 | PB-10 | 480 | 0 | 18.3 | 8784 | 4 | 5.4461 | 11.2774 | 2.3495 | PB-6
PB-10 | L-14 | 16 | 3.66 | 21.96 | 351.36 | 4 | 0.21784 | 11.4952 | 2.3948 | PB-10
PB-10 | PB-18 | 331 | 0 | 21.96 | 7268.76 | 4 | 4.5066 | 16.0018 | 3.3337 | PB-10
PB-18 | PB-19 | 147 | 0 | 21.96 | 3228.12 | 4 | 2.0014 | 18.0033 | 3.7507 | PB-18
PB-19 | CC-2 | 45 | 0 | 21.96 | 988.2 | 4 | 0.61268 | 18.616 | 3.8783 | PB-19