## WEST CIRCUIT
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | MOT | 725 | 14.41 |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | Controller | Circuit: | 2 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
L-1 | L-2 | 102 | 0.3 | 0.3 | 30.6 | 4 | 0.018972 | 0.018972 | 0.007905 | L-1
L-2 | L-3 | 120 | 0.3 | 0.6 | 72 | 4 | 0.04464 | 0.063612 | 0.026505 | L-2
L-3 | L-4 | 98 | 0.3 | 0.9 | 88.2 | 4 | 0.054684 | 0.1183 | 0.04929 | L-3
L-4 | PB-1 | 25 | 0.3 | 1.2 | 30 | 4 | 0.0186 | 0.1369 | 0.05704 | L-4
PB-1 | PB-2 | 59 | 0 | 1.2 | 70.8 | 4 | 0.043896 | 0.18079 | 0.07533 | PB-1
PB-2 | PB-3 | 52 | 0 | 1.2 | 62.4 | 4 | 0.038688 | 0.21948 | 0.09145 | PB-2
PB-3 | PB-4 | 53 | 0 | 1.2 | 63.6 | 4 | 0.039432 | 0.25891 | 0.10788 | PB-3
PB-4 | L-5 | 33 | 0 | 1.2 | 39.6 | 4 | 0.024552 | 0.28346 | 0.11811 | PB-4
L-5 | L-6 | 142 | 0.3 | 1.5 | 213 | 4 | 0.13206 | 0.41552 | 0.17314 | L-5
L-6 | L-7 | 145 | 0.3 | 1.8 | 261 | 4 | 0.16182 | 0.57734 | 0.24056 | L-6
L-7 | PB-7 | 62 | 0.3 | 2.1 | 130.2 | 4 | 0.080724 | 0.65807 | 0.27419 | L-7
PB-7 | PB-8 | 10 | 0 | 2.1 | 21 | 4 | 0.01302 | 0.67109 | 0.27962 | PB-7
PB-8 | L-8 | 20 | 0.052 | 2.152 | 43.04 | 4 | 0.026685 | 0.69777 | 0.29074 | PB-8
L-8 | L-9 | 43 | 0.052 | 2.204 | 94.772 | 4 | 0.058759 | 0.75653 | 0.31522 | L-8
PB-7 | PB-9 | 153 | 0 | 2.204 | 337.212 | 4 | 0.20907 | 0.9656 | 0.40233 | PB-7
PB-9 | L-10 | 8 | 0.3 | 2.504 | 20.032 | 4 | 0.01242 | 0.97802 | 0.40751 | PB-9
PB-9 | PB-11 | 77 | 0 | 2.504 | 192.808 | 4 | 0.11954 | 1.0976 | 0.45732 | PB-9
PB-11 | PB-12 | 8 | 0 | 2.504 | 20.032 | 4 | 0.01242 | 1.11 | 0.46249 | PB-11
PB-12 | L-11 | 24 | 0.052 | 2.556 | 61.344 | 4 | 0.038033 | 1.148 | 0.47834 | PB-12
L-11 | L-12 | 43 | 0.052 | 2.608 | 112.144 | 4 | 0.069529 | 1.2175 | 0.50731 | L-11
PB-11 | PB-13 | 139 | 0 | 2.608 | 362.512 | 4 | 0.22476 | 1.4423 | 0.60096 | PB-11
PB-13 | L-13 | 11 | 0 | 2.608 | 28.688 | 4 | 0.017787 | 1.4601 | 0.60837 | PB-13
L-13 | L-15 | 102 | 0.3 | 2.908 | 296.616 | 4 | 0.1839 | 1.644 | 0.685 | L-13
L-15 | PB-14 | 47 | 0.3 | 3.208 | 150.776 | 4 | 0.093481 | 1.7375 | 0.72395 | L-15
PB-14 | CC-1 | 8 | 0 | 3.208 | 25.664 | 4 | 0.015912 | 1.7534 | 0.73058 | PB-14

## EAST CIRCUIT
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | MOT | 725 | 14.41 |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | Controller | Circuit: | 2 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
L-29 | PB-25 | 16 | 0.3 | 0.3 | 4.8 | 4 | 0.002976 | 0.002976 | 0.00124 | L-29
PB-25 | L-28 | 77 | 0 | 0.3 | 23.1 | 4 | 0.014322 | 0.017298 | 0.0072075 | PB-25
L-28 | L-27 | 91 | 0.3 | 0.6 | 54.6 | 4 | 0.033852 | 0.05115 | 0.021313 | L-28
L-27 | L-26 | 90 | 0.3 | 0.9 | 81 | 4 | 0.05022 | 0.10137 | 0.042237 | L-27
L-26 | L-25 | 91 | 0.3 | 1.2 | 109.2 | 4 | 0.067704 | 0.16907 | 0.070447 | L-26
L-25 | L-23 | 89 | 0.3 | 1.5 | 133.5 | 4 | 0.08277 | 0.25184 | 0.10494 | L-25
L-23 | PB-24 | 5 | 0.3 | 1.8 | 9 | 4 | 0.00558 | 0.25742 | 0.10726 | L-23
PB-24 | PB-23 | 117 | 0 | 1.8 | 210.6 | 4 | 0.13057 | 0.388 | 0.16167 | PB-24
PB-23 | PB-22 | 118 | 0 | 1.8 | 212.4 | 4 | 0.13169 | 0.51968 | 0.21654 | PB-23
PB-22 | L-22 | 16 | 0 | 1.8 | 28.8 | 4 | 0.017856 | 0.53754 | 0.22398 | PB-22
L-22 | PB-21 | 85 | 0.3 | 2.1 | 178.5 | 4 | 0.11067 | 0.64821 | 0.27009 | L-22
PB-21 | L-21 | 17 | 0 | 2.1 | 35.7 | 4 | 0.022134 | 0.67034 | 0.27931 | PB-21
L-21 | L-20 | 95 | 0.3 | 2.4 | 228 | 4 | 0.14136 | 0.8117 | 0.33821 | L-21
L-20 | L-19 | 116 | 0.3 | 2.7 | 313.2 | 4 | 0.19418 | 1.0059 | 0.41912 | L-20
L-19 | L-18 | 105 | 0.3 | 3 | 315 | 4 | 0.1953 | 1.2012 | 0.50049 | L-19
L-18 | L-17 | 94 | 0.3 | 3.3 | 310.2 | 4 | 0.19232 | 1.3935 | 0.58063 | L-18
L-17 | PB-17 | 19 | 0.3 | 3.6 | 68.4 | 4 | 0.042408 | 1.4359 | 0.5983 | L-17
PB-17 | PB-16 | 43 | 0 | 3.6 | 154.8 | 4 | 0.095976 | 1.5319 | 0.63829 | PB-17
PB-16 | PB-15 | 79 | 0 | 3.6 | 284.4 | 4 | 0.17633 | 1.7082 | 0.71176 | PB-16
PB-15 | L-16 | 6 | 0.3 | 3.9 | 23.4 | 4 | 0.014508 | 1.7227 | 0.71781 | PB-15
PB-15 | PB-14 | 61 | 0 | 3.9 | 237.9 | 4 | 0.1475 | 1.8702 | 0.77926 | PB-15
PB-14 | CC-1 | 8 | 0 | 3.9 | 31.2 | 4 | 0.019344 | 1.8896 | 0.78732 | PB-14