## I-71 at SR-38
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 3 | 12 | 2
Power Service: |  |  | Circuit: | [7 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 1/0 | AWG. | 0.12 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 120 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
PS-1 | PB-1 | 5 | 0 | 30 | 150 | 1/0 | 0.036 | 0.036 | 0.03 | PB-1
PB-1 | PB-2 | 250 | 0 | 30 | 7500 | 1/0 | 1.8 | 1.836 | 1.53 | PB-2
PB-2 | PB-3 | 108 | 0 | 30 | 3240 | 1/0 | 0.7776 | 2.6136 | 2.178 | PB-3
PB-3 | PB-4 | 63 | 0 | 30 | 1890 | 1/0 | 0.4536 | 3.0672 | 2.556 | PB-4
PB-4 | PB-5 | 341 | 0 | 30 | 10230 | 1/0 | 2.4552 | 5.5224 | 4.602 | PB-5
PB-5 | CABINET | 15 | 30 | 30 | 450 | 1/0 | 0.108 | 5.6304 | 4.692 | CABINET
120
240
480

## I-270 at US-33
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 3 | 12 | 2
Power Service: |  |  | Circuit: | [7 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
PS-1 | PB-1 | 5 | 0 | 7.5 | 37.5 | 6 | 0.03675 | 0.03675 | 0.0076562 | PB-1
PB-1 | PB-2 | 37 | 0 | 7.5 | 277.5 | 6 | 0.27195 | 0.3087 | 0.064312 | PB-2
PB-2 | PB-3 | 361 | 0 | 7.5 | 2707.5 | 6 | 2.6534 | 2.9621 | 0.61709 | PB-3
PB-3 | PB-4 | 58 | 0 | 7.5 | 435 | 6 | 0.4263 | 3.3883 | 0.70591 | PB-4
PB-4 | PB-5 | 505 | 0 | 7.5 | 3787.5 | 6 | 3.7117 | 7.1001 | 1.4792 | PB-5
PB-5 | PB-6 | 378 | 0 | 7.5 | 2835 | 6 | 2.7783 | 9.8784 | 2.058 | PB-6
PB-6 | PB-7 | 53 | 0 | 7.5 | 397.5 | 6 | 0.38955 | 10.2679 | 2.1392 | PB-7
PB-7 | PB-8 | 76 | 0 | 7.5 | 570 | 6 | 0.5586 | 10.8265 | 2.2555 | PB-8
PB-8 | PB-9 | 148 | 0 | 7.5 | 1110 | 6 | 1.0878 | 11.9143 | 2.4822 | PB-9
PB-9 | XMFR | 15 | 7.5 | 7.5 | 112.5 | 6 | 0.11025 | 12.0246 | 2.5051 | XMFR
XMFR | PB-10 | 10 | 0 | 30 | 300 | 6 | 0.294 | 12.3186 | 2.5664 | PB-10
PB-10 | CABINET | 20 | 30 | 30 | 600 | 6 | 0.588 | 12.6126 | 2.6276 | CABINET
120
240
480