## I-70 WB @ Hamilton
I-70 WB @ HAMILTON ROAD
Item | Quantity | Watts/unit | Total Watts
3-Section 12 in. head | 8 | 13 | 104
5-Section 12 in. head | 1 | 25 | 25
Pedestrian Signal Head | 2 | 21 | 42
8-Phase Control Cabinet | 1 | 300 | 300
Stop-Line Radar Unit | 2 | 9 | 18
Dilemma Zone Radar Unit | 2 | 3.2 | 6.4
|  | Total | 495.4
Volts = 120V
i = Amps = watts/volts | 4.1283
L (ft) | 567
R (ohms/1000ft) | 0.51
Voltage Drop Calculation | (2 x R x L x i)/1000
Voltage Drop = | 2.3876 | %

## I-70 EB @ Hamilton
I-70 EB @ HAMILTON ROAD
Item | Quantity | Watts/unit | Total Watts
3-Section 12 in. head | 7 | 13 | 91
5-Section 12 in. head | 1 | 25 | 25
Pedestrian Signal Head | 2 | 21 | 42
8-Phase Control Cabinet | 1 | 300 | 300
Stop-Line Radar Unit | 2 | 9 | 18
Dilemma Zone Radar Unit | 2 | 3.2 | 6.4
|  | Total | 482.4
Volts = 120V
i = Amps = watts/volts | 4.02
L (ft) | 1002
R (ohms/1000ft) | 0.51 | No. 6 AWG
Voltage Drop Calculation= | (2 x R x L x i)/1000
Voltage Drop = | 4.1086 | %