## H13 - MAGENTA (2) (hidden)
| I66 OTB | [10 empty] | CALC. | CHECK.
JGM
2018-06-28
|  |  |  | Voltage: | 277/480 | Volts |  |  |  | - ΦA (277V) - |  |  |  | Line Volts |  | 1 | 1
|  |  |  | Number Wire System: | 4 | WIRE |  |  |  | - ΦB (277V) - |  |  |  | 277 |  | 4 | 12
|  |  |  | Wire Gage: | 2 | AWG |  |  |  | - ΦC (277V) - | [5 empty] | 150 | 90
- N -
| CIRCUITS 1A, 3B & 5C | [14 empty] | 600 | 1080
Phase | Section |  |  |  | Watts | Current (Amps) |  | Ampere- | Wire Resistance (Ohms/1000 FT) | Voltage Drop |  | % Drop | At Point |  |  | 1680
| From | To | Dist. (ft) | Dist. + Slack (ft) | At Point | At Point | Accum. | Feet |  | In Section | Accum. | [5 empty] | #REF!
1A | 170 | HH | 790 | 805 | 244 | 0.91 | 0.91 | 1465.1 | 0.1624 | 0.23793 | 2.9699 | 1.072% | 170
1A | 166 | HH | 10 | 25 | 244 | 0.91 | 0.91 | 45.5 | 0.1624 | 0.0073892 | 2.7393 | 0.9889% | 166
1A | 169 | HH | 560 | 575 | 244 | 0.91 | 0.91 | 1046.5 | 0.1624 | 0.16995 | 2.9258 | 1.056% | 169
1A | HH | HH | 66 | 81 | 0 | 0 | 0.91 | 147.42 | 0.1624 | 0.023941 | 2.7559 | 0.9949% | HH
1A | HH | HH | 140 | 155 | 0 | 0 | 2.73 | 846.3 | 0.1624 | 0.13744 | 2.7319 | 0.9863% | HH
1A | 154 | HH | 195 | 210 | 244 | 0.91 | 0.91 | 382.2 | 0.1624 | 0.062069 | 2.6566 | 0.959% | 154
1A | HH | HH | 75 | 90 | 0 | 0 | 3.64 | 655.2 | 0.1624 | 0.1064 | 2.5945 | 0.9366% | HH
1A | 163 | 160 | 661 | 676 | 244 | 0.91 | 0.91 | 1230.32 | 0.1624 | 0.1998 | 3.8702 | 1.397% | 163
1A | 160 | 157 | 650 | 665 | 244 | 0.91 | 1.82 | 2420.6 | 0.1624 | 0.39311 | 3.6704 | 1.325% | 160
1A | 157 | HH | 875 | 890 | 244 | 0.91 | 2.73 | 4859.4 | 0.1624 | 0.78917 | 3.2773 | 1.183% | 157
1A | HH | 151 | 215 | 230 | 0 | 0 | 2.73 | 1255.8 | 0.1624 | 0.20394 | 2.4881 | 0.8982% | HH
1A | 151 | 148 | 600 | 615 | 244 | 0.91 | 3.64 | 4477.2 | 0.1624 | 0.7271 | 2.2841 | 0.8246% | 151
1A | 148 | HH | 585 | 600 | 244 | 0.91 | 4.55 | 5460 | 0.1624 | 0.8867 | 1.5571 | 0.5621% | 148
1A | 136 | 139 | 595 | 610 | 244 | 0.91 | 0.91 | 1110.2 | 0.1624 | 0.1803 | 1.3088 | 0.4725% | 136
1A | 139 | HH | 595 | 610 | 244 | 0.91 | 1.82 | 2220.4 | 0.1624 | 0.36059 | 1.1285 | 0.4074% | 139
1A | HH | HH | 150 | 165 | 0 | 0 | 1.82 | 600.6 | 0.1624 | 0.097537 | 0.76789 | 0.2772% | HH
1A | 142 | 145 | 705 | 720 | 244 | 0.91 | 0.91 | 1310.4 | 0.1624 | 0.21281 | 1.0233 | 0.3694% | 142
1A | 145 | HH | 222 | 237 | 244 | 0.91 | 1.82 | 862.68 | 0.1624 | 0.1401 | 0.81045 | 0.2926% | 145
1A | HH | HH | 76 | 91 | 0 | 0 | 8.19 | 1490.58 | 0.1624 | 0.24207 | 0.67035 | 0.242% | HH
1A | HH | HH | 121 | 136 | 0 | 0 | 8.19 | 2227.68 | 0.1624 | 0.36178 | 0.42828 | 0.1546% | HH
1A | HH | CCW | 10 | 25 | 0 | 0 | 8.19 | 409.5 | 0.1624 | 0.066503 | 0.066503 | 0.02401% | HH
3B | 171 | 167 | 790 | 805 | 244 | 0.91 | 0.91 | 1465.1 | 0.1624 | 0.23793 | 4.738 | 1.71% | 171
3B | 167 | HH | 202 | 217 | 244 | 0.91 | 1.82 | 789.88 | 0.1624 | 0.12828 | 4.5 | 1.625% | 167
3B | HH | HH | 212 | 227 | 0 | 0 | 1.82 | 826.28 | 0.1624 | 0.13419 | 4.3717 | 1.578% | HH
3B | 164 | 161 | 663 | 678 | 244 | 0.91 | 0.91 | 1233.96 | 0.1624 | 0.2004 | 5.9477 | 2.147% | 164
3B | 161 | 158 | 681 | 696 | 244 | 0.91 | 1.82 | 2533.44 | 0.1624 | 0.41143 | 5.7473 | 2.075% | 161
3B | 158 | 155 | 645 | 660 | 244 | 0.91 | 2.73 | 3603.6 | 0.1624 | 0.58522 | 5.3359 | 1.926% | 158
3B | 155 | HH | 419 | 434 | 244 | 0.91 | 3.64 | 3159.52 | 0.1624 | 0.51311 | 4.7507 | 1.715% | 155
3B | HH | 152 | 21 | 36 | 0 | 0 | 5.46 | 393.12 | 0.1624 | 0.063843 | 4.2376 | 1.53% | HH
3B | 152 | 149 | 585 | 600 | 244 | 0.91 | 6.37 | 7644 | 0.1624 | 1.2414 | 4.1737 | 1.507% | 152
3B | 149 | 146 | 675 | 690 | 244 | 0.91 | 7.28 | 10046.4 | 0.1624 | 1.6315 | 2.9323 | 1.059% | 149
3B | 146 | HH | 110 | 125 | 244 | 0.91 | 8.19 | 2047.5 | 0.1624 | 0.33251 | 1.3008 | 0.4696% | 146
3B | 134 | 137 | 125 | 140 | 244 | 0.91 | 0.91 | 254.8 | 0.1624 | 0.04138 | 1.9114 | 0.69% | 134
3B | 137 | 140 | 705 | 720 | 244 | 0.91 | 1.82 | 2620.8 | 0.1624 | 0.42562 | 1.8701 | 0.6751% | 137
3B | 140 | HH | 357 | 372 | 244 | 0.91 | 2.73 | 2031.12 | 0.1624 | 0.32985 | 1.4444 | 0.5215% | 140
3B | HH | HH | 150 | 165 | 0 | 0 | 2.73 | 900.9 | 0.1624 | 0.14631 | 1.1146 | 0.4024% | HH
3B | 143 | HH | 690 | 705 | 244 | 0.91 | 0.91 | 1283.1 | 0.1624 | 0.20838 | 1.1767 | 0.4248% | 143
3B | HH | HH | 76 | 91 | 0 | 0 | 11.83 | 2153.06 | 0.1624 | 0.34966 | 0.96828 | 0.3496% | HH
3B | HH | HH | 121 | 136 | 0 | 0 | 11.83 | 3217.76 | 0.1624 | 0.52256 | 0.61862 | 0.2233% | HH
3B | HH | CCW | 10 | 25 | 0 | 0 | 11.83 | 591.5 | 0.1624 | 0.09606 | 0.09606 | 0.03468% | HH
5C | 172 | 168 | 807 | 822 | 244 | 0.91 | 0.91 | 1496.04 | 0.1624 | 0.24296 | 5.0755 | 1.832% | 172
5C | 168 | HH | 405 | 420 | 244 | 0.91 | 1.82 | 1528.8 | 0.1624 | 0.24828 | 4.8325 | 1.745% | 168
5C | 165 | HH | 202 | 217 | 244 | 0.91 | 0.91 | 394.94 | 0.1624 | 0.064138 | 4.6484 | 1.678% | 165
5C | HH | HH | 140 | 155 | 0 | 0 | 2.73 | 846.3 | 0.1624 | 0.13744 | 4.5843 | 1.655% | HH
5C | 153 | HH | 206 | 221 | 244 | 0.91 | 0.91 | 402.22 | 0.1624 | 0.065321 | 4.5121 | 1.629% | 153
5C | HH | HH | 75 | 90 | 0 | 0 | 3.64 | 655.2 | 0.1624 | 0.1064 | 4.4468 | 1.605% | HH
5C | 162 | 159 | 645 | 660 | 244 | 0.91 | 0.91 | 1201.2 | 0.1624 | 0.19507 | 5.4585 | 1.971% | 162
5C | 159 | 156 | 672 | 687 | 244 | 0.91 | 1.82 | 2500.68 | 0.1624 | 0.40611 | 5.2635 | 1.9% | 159
5C | 156 | HH | 568 | 583 | 244 | 0.91 | 2.73 | 3183.18 | 0.1624 | 0.51695 | 4.8574 | 1.754% | 156
5C | HH | 150 | 409 | 424 | 0 | 0 | 6.37 | 5401.76 | 0.1624 | 0.87725 | 4.3404 | 1.567% | HH
5C | 150 | 147 | 625 | 640 | 244 | 0.91 | 7.28 | 9318.4 | 0.1624 | 1.5133 | 3.4632 | 1.25% | 150
5C | 147 | HH | 354 | 369 | 244 | 0.91 | 8.19 | 6044.22 | 0.1624 | 0.98158 | 1.9499 | 0.7039% | 147
5C | 135 | 138 | 485 | 500 | 244 | 0.91 | 0.91 | 910 | 0.1624 | 0.14778 | 1.8337 | 0.662% | 135
5C | 138 | 141 | 626 | 641 | 244 | 0.91 | 1.82 | 2333.24 | 0.1624 | 0.37892 | 1.6859 | 0.6086% | 138
5C | 141 | HH | 202 | 217 | 244 | 0.91 | 2.73 | 1184.82 | 0.1624 | 0.19241 | 1.307 | 0.4718% | 141
5C | HH | HH | 150 | 165 | 0 | 0 | 2.73 | 900.9 | 0.1624 | 0.14631 | 1.1146 | 0.4024% | HH
5C | 144 | HH | 456 | 471 | 244 | 0.91 | 0.91 | 857.22 | 0.1624 | 0.13921 | 1.1075 | 0.3998% | 144
5C | HH | HH | 76 | 91 | 0 | 0 | 11.83 | 2153.06 | 0.1624 | 0.34966 | 0.96828 | 0.3496% | HH
5C | HH | HH | 121 | 136 | 0 | 0 | 11.83 | 3217.76 | 0.1624 | 0.52256 | 0.61862 | 0.2233% | HH
5C | HH | CCW | 10 | 25 | 0 | 0 | 11.83 | 591.5 | 0.1624 | 0.09606 | 0.09606 | 0.03468% | HH
|  |  |  | Total = | [5 empty] | MAX VOLTAGE DROP:
|  |  |  | 1A | 3172 | 11.83 |  |  |  | 1A | 3.8702 | 1.397%
|  |  |  | 3B | 3172 | 11.83 |  |  |  | 3B | 5.9477 | 2.147%
|  |  |  | 5C | 3172 | 11.83 |  |  |  | 5C | 5.4585 | 1.971%
VDOT TEDM says 3% max voltage drop to allow for expansion & field modifications. Assume no expansion on this project, so go slightly beyond 3%
| 0 |  |  | 23267
| Line Operating Amps = (Lamp Watts + LED Driver Watts)/Line voltage | [13 empty] | AWG | OHMS/1000FT
| - MH Ballast Watts assumed to be 30% lamp watts. | [13 empty] | 14 | 2.624
[15 empty] | 12 | 1.65
| Lamp Wattage |  | Wattage | Driver/ Ballast Amps | Line Amps, Operating |  |  | Otain wire resistance from published data | [6 empty] | 10 | 1.038
[5 empty] | Volts | [9 empty] | 8 | 0.6528
[5 empty] | 277/480 | 240 |  | Wire Size | ohms per 1000 ft | [5 empty] | 6 | 0.4105
| Philips RFL 241W |  | 244 | n/a | 0.91 |  |  | 2 | 0.1624 | [5 empty] | 4 | 0.2582
[15 empty] | 2 | 0.1624
| Voltage Drop = (Amperes Accum.)* [(Length of section * 2wires)/1000]*Resistance wire per 1000 ft | [13 empty] | 1/0 | 0.1021
| Allow 5 to 10 ft allowance per connection or round up to the nearest 5 ft. | [13 empty] | 2/0 | 0.08097
| Channel and Aerial Hazard Lights have 2 lights per location | [13 empty] | 4/0 | 0.05093

## D
FRA-270-36.94 | [13 empty] | CALC. | CHECK.
JGM
[9 empty] | - L1 (480V) - |  |  |  |  | 11/14/2022
|  |  | Voltage: | 480 | Volts |  |  |  | - N - |  |  |  | Line Volts
|  |  | Number Wire System: | 3 | WIRE |  |  |  | - G - |  |  |  | 480
|  |  | Wire Gage: | 4 | AWG
Circuit D
Section |  |  |  | Watts | Current (Amps) |  | Ampere- | Wire Resistance (Ohms/1000 FT) | Voltage Drop |  | % Drop | At Point
From | To | Dist. (ft) | Dist. + Slack (ft) | At Point | At Point | Accum. | Feet |  | In Section | Accum.
D-20 | D-19 | 360 | 375 | 166 | 0.34583 | 0.34583 | 259.375 | 0.2582 | 0.066971 | 4.6 | 0.9583% | D-20
D-19 | D-18 | 180 | 195 | 166 | 0.34583 | 0.69167 | 269.75 | 0.2582 | 0.069649 | 4.533 | 0.9444% | D-19
D-18 | D-17 | 85 | 100 | 166 | 0.34583 | 1.0375 | 207.5 | 0.2582 | 0.053577 | 4.4634 | 0.9299% | D-18
D-17 | D-16 | 215 | 230 | 166 | 0.34583 | 1.3833 | 636.3333 | 0.2582 | 0.1643 | 4.4098 | 0.9187% | D-17
D-16 | D-33 | 400 | 415 | 166 | 0.34583 | 1.7292 | 1435.2083 | 0.2582 | 0.37057 | 4.2455 | 0.8845% | D-16
D-33 | D-32 | 60 | 75 | 176 | 0.36667 | 2.0958 | 314.375 | 0.2582 | 0.081172 | 3.8749 | 0.8073% | D-33
D-32 | D-31 | 120 | 135 | 176 | 0.36667 | 2.4625 | 664.875 | 0.2582 | 0.17167 | 3.7937 | 0.7904% | D-32
D-31 | D-30 | 60 | 75 | 176 | 0.36667 | 2.8292 | 424.375 | 0.2582 | 0.10957 | 3.6221 | 0.7546% | D-31
D-30 | D-14 | 155 | 170 | 176 | 0.36667 | 3.1958 | 1086.5833 | 0.2582 | 0.28056 | 3.5125 | 0.7318% | D-30
D-14 | D-3 | 170 | 185 | 166 | 0.34583 | 3.5417 | 1310.4167 | 0.2582 | 0.33835 | 3.2319 | 0.6733% | D-14
D-13 | D-12 | 275 | 290 | 166 | 0.34583 | 0.34583 | 200.5833 | 0.2582 | 0.051791 | 6.6047 | 1.376% | D-13
D-12 | D-11 | 275 | 290 | 166 | 0.34583 | 0.69167 | 401.1667 | 0.2582 | 0.10358 | 6.5529 | 1.365% | D-12
D-11 | EX PB #1 | 340 | 355 | 166 | 0.34583 | 1.0375 | 736.625 | 0.2582 | 0.1902 | 6.4493 | 1.344% | D-11
UP-4 | UP-3 | 20 | 35 | 250 | 0.67708 | 0.67708 | 47.3958 | 0.2582 | 0.012238 | 6.4095 | 1.335% | UP-4
UP-3 | UP-2 | 20 | 35 | 250 | 0.67708 | 1.3542 | 94.7917 | 0.2582 | 0.024475 | 6.3972 | 1.333% | UP-3
UP-2 | UP-1 | 20 | 35 | 250 | 0.67708 | 2.0312 | 142.1875 | 0.2582 | 0.036713 | 6.3728 | 1.328% | UP-2
UP-1 | EX PB #1 | 40 | 55 | 250 | 0.67708 | 2.7083 | 297.9167 | 0.2582 | 0.076922 | 6.3361 | 1.32% | UP-1
EX PB #1 | D-10 | 45 | 60 | 0 | 0.34583 | 4.0917 | 491 | 0.2582 | 0.12678 | 6.2591 | 1.304% | EX PB #1
D-10 | D-9 | 163 | 178 | 166 | 0.34583 | 4.4375 | 1579.75 | 0.2582 | 0.40789 | 6.1324 | 1.278% | D-10
D-9 | D-8 | 150 | 165 | 166 | 0.34583 | 4.7833 | 1578.5 | 0.2582 | 0.40757 | 5.7245 | 1.193% | D-9
D-8 | D-7 | 140 | 155 | 166 | 0.34583 | 5.1292 | 1590.0417 | 0.2582 | 0.41055 | 5.3169 | 1.108% | D-8
D-7 | D-6 | 150 | 165 | 166 | 0.34583 | 5.475 | 1806.75 | 0.2582 | 0.4665 | 4.9063 | 1.022% | D-7
D-6 | D-5 | 140 | 155 | 166 | 0.34583 | 5.8208 | 1804.4583 | 0.2582 | 0.46591 | 4.4398 | 0.925% | D-6
D-5 | D-4 | 150 | 165 | 166 | 0.34583 | 6.1667 | 2035 | 0.2582 | 0.52544 | 3.9739 | 0.8279% | D-5
D-4 | D-3 | 150 | 165 | 166 | 0.34583 | 6.5125 | 2149.125 | 0.2582 | 0.5549 | 3.4485 | 0.7184% | D-4
D-3 | D-2 | 90 | 105 | 166 | 0.34583 | 10.4 | 2184 | 0.2582 | 0.56391 | 2.8936 | 0.6028% | D-3
D-2 | D-1 | 250 | 265 | 166 | 0.34583 | 10.7458 | 5695.2917 | 0.2582 | 1.4705 | 2.3297 | 0.4854% | D-2
D-1 | EX CC: H-1 | 135 | 150 | 166 | 0.34583 | 11.0917 | 3327.5 | 0.2582 | 0.85916 | 0.85916 | 0.179% | D-1
EX CC: H-1
|  |  | Total = | [5 empty] | MAX VOLTAGE DROP:
|  |  | D | 4858 | 11.0917 |  |  |  | D | 6.6047 | 1.376%
VDOT TEDM says 3% max voltage drop to allow for expansion & field modifications. Assume no expansion on this project, so go slightly beyond 3%
0 |  |  | 4778
### = Branch in Circuit
[16 empty] | AWG | OHMS/1000FT
[16 empty] | 14 | 2.624
[16 empty] | 12 | 1.65
Lamp Wattage |  | Wattage | Driver/ Ballast Amps | Line Amps, Operating |  |  | Otain wire resistance from published data | [8 empty] | 10 | 1.038
|  |  |  | Volts | [11 empty] | 8 | 0.6528
|  |  |  | 480 | 240 |  | Wire Size | ohms per 1000 ft | [7 empty] | 6 | 0.4105
(2) - Sternberg 1531 LED Omega Series |  | 176 | n/a | 0.36667 | - |  | 4 | 0.2582 | [7 empty] | 4 | 0.2582
[16 empty] | 2 | 0.1624
Existing LED Conventional Cobrehead * |  | 166 | n/a | 0.34583 | -
Existing Underpass Lighting |  | 250 | 30% | 0.67708 | -
Voltage Drop = (Amperes Accum.)* [(Length of section * 2wires)/1000]*Resistance wire per 1000 ft | [15 empty] | 1/0 | 0.1021
Allow 15 ft allowance per connection. | [15 empty] | 2/0 | 0.08097
* No existing plans are available for the current luminaires on conventional light poles in this area. Field images show that the current fixtures are LED style luminaires. An ODOT approved solid-state LED, per Supplemental Spec 813, has been used as a placeholder until further information is received. The luminaire is based the Cooper Navion Series (NVN), 3-light square, 1050 mA option (SA3C). | [15 empty] | 4/0 | 0.05093

## B
FRA-270-36.94 | [13 empty] | CALC. | CHECK.
JGM
[9 empty] | - L1 (480V) - |  |  |  |  | 11/14/2022
|  |  | Voltage: | 480 | Volts |  |  |  | - N - |  |  |  | Line Volts
|  |  | Number Wire System: | 3 | WIRE |  |  |  | - G - |  |  |  | 480
|  |  | Wire Gage: | 4 | AWG
Circuit B
Section |  |  |  | Watts | Current (Amps) |  | Ampere- | Wire Resistance (Ohms/1000 FT) | Voltage Drop |  | % Drop | At Point
From | To | Dist. (ft) | Dist. + Slack (ft) | At Point | At Point | Accum. | Feet |  | In Section | Accum.
B-18 | B-15 | 685 | 700 | 166 | 0.34583 | 0.34583 | 484.1667 | 0.2582 | 0.12501 | 5.2968 | 1.104% | B-18
B-15 | B-14 | 400 | 415 | 166 | 0.34583 | 0.69167 | 574.0833 | 0.2582 | 0.14823 | 5.1718 | 1.077% | B-15
B-14 | EX PB #2 | 260 | 275 | 166 | 0.34583 | 1.0375 | 570.625 | 0.2582 | 0.14734 | 5.0236 | 1.047% | B-14
B-13 | EX PB #2 | 100 | 115 | 166 | 0.34583 | 0.34583 | 79.5417 | 0.2582 | 0.020538 | 4.8968 | 1.02% | B-13
EX PB #2 | B-12 | 150 | 165 | 0 | 0 | 1.3833 | 456.5 | 0.2582 | 0.11787 | 4.8762 | 1.016% | EX PB #2
B-12 | EX PB #3 | 70 | 85 | 166 | 0.34583 | 1.7292 | 293.9583 | 0.2582 | 0.0759 | 4.7584 | 0.9913% | B-12
B-11 | B-10 | 190 | 205 | 166 | 0.34583 | 0.34583 | 141.7917 | 0.2582 | 0.036611 | 5.5692 | 1.16% | B-11
B-10 | B-9 | 150 | 165 | 166 | 0.34583 | 0.69167 | 228.25 | 0.2582 | 0.058934 | 5.5325 | 1.153% | B-10
B-9 | B-8 | 145 | 160 | 166 | 0.34583 | 1.0375 | 332 | 0.2582 | 0.085722 | 5.4736 | 1.14% | B-9
B-8 | B-7 | 135 | 150 | 166 | 0.34583 | 1.3833 | 415 | 0.2582 | 0.10715 | 5.3879 | 1.122% | B-8
B-7 | B-6 | 140 | 155 | 166 | 0.34583 | 1.7292 | 536.0417 | 0.2582 | 0.13841 | 5.2807 | 1.1% | B-7
B-6 | B-5 | 140 | 155 | 166 | 0.34583 | 2.075 | 643.25 | 0.2582 | 0.16609 | 5.1423 | 1.071% | B-6
B-5 | B-4 | 140 | 155 | 166 | 0.34583 | 2.4208 | 750.4583 | 0.2582 | 0.19377 | 4.9762 | 1.037% | B-5
B-4 | EX PB #3 | 55 | 70 | 166 | 0.34583 | 2.7667 | 387.3333 | 0.2582 | 0.10001 | 4.7825 | 0.9963% | B-4
EX PB #3 | B-3 | 120 | 135 | 0 | 0 | 4.4958 | 1213.875 | 0.2582 | 0.31342 | 4.6825 | 0.9755% | EX PB #3
B-3 | B-33 | 180 | 195 | 166 | 0.34583 | 4.8417 | 1888.25 | 0.2582 | 0.48755 | 4.369 | 0.9102% | B-3
B-33 | B-32 | 60 | 75 | 176 | 0.36667 | 5.2083 | 781.25 | 0.2582 | 0.20172 | 3.8815 | 0.8086% | B-33
B-32 | B-31 | 120 | 135 | 176 | 0.36667 | 5.575 | 1505.25 | 0.2582 | 0.38866 | 3.6798 | 0.7666% | B-32
B-31 | B-30 | 60 | 75 | 176 | 0.36667 | 5.9417 | 891.25 | 0.2582 | 0.23012 | 3.2911 | 0.6857% | B-31
B-30 | B-1 | 412 | 427 | 176 | 0.36667 | 6.3083 | 5387.3167 | 0.2582 | 1.391 | 3.061 | 0.6377% | B-30
B-1 | EX CC: H-1 | 471 | 486 | 166 | 0.34583 | 6.6542 | 6467.85 | 0.2582 | 1.67 | 1.67 | 0.3479% | B-1
EX CC: H-1
|  |  | Total = | [5 empty] | MAX VOLTAGE DROP:
|  |  | B | 3194 | 6.6542 |  |  |  | B | 5.5692 | 1.16%
VDOT TEDM says 3% max voltage drop to allow for expansion & field modifications. Assume no expansion on this project, so go slightly beyond 3%
0 |  |  | 4498
### = Branch in Circuit
[16 empty] | AWG | OHMS/1000FT
[16 empty] | 14 | 2.624
[16 empty] | 12 | 1.65
Lamp Wattage |  | Wattage | Driver/ Ballast Amps | Line Amps, Operating |  |  | Otain wire resistance from published data | [8 empty] | 10 | 1.038
|  |  |  | Volts | [11 empty] | 8 | 0.6528
|  |  |  | 480 | 240 |  | Wire Size | ohms per 1000 ft | [7 empty] | 6 | 0.4105
(2) - Sternberg 1531 LED Omega Series |  | 176 | n/a | 0.36667 | - |  | 4 | 0.2582 | [7 empty] | 4 | 0.2582
[16 empty] | 2 | 0.1624
Existing LED Conventional Cobrehead |  | 166 | n/a | 0.34583 | -
Voltage Drop = (Amperes Accum.)* [(Length of section * 2wires)/1000]*Resistance wire per 1000 ft | [15 empty] | 1/0 | 0.1021
Allow 5 to 10 ft allowance per connection or round up to the nearest 5 ft. | [15 empty] | 2/0 | 0.08097
* No existing plans are available for the current luminaires on conventional light poles in this area. Field images show that the current fixtures are LED style luminaires. An ODOT approved solid-state LED, per Supplemental Spec 813, has been used as a placeholder until further information is received. The luminaire is based the Cooper Navion Series (NVN), 3-light square, 1050 mA option (SA3C). | [15 empty] | 4/0 | 0.05093

## CONTROL CENTER DATA TABLE
CONTROL CENTER DATA
CONTROL CENTER DESIGNATION | LINE VOLTS | CONNECTED LOAD (KVA) | SERVICE ENTRANCE CONDUCTOR SIZE - AWG | ENCLOSURE RATING (AMPS) | CIRCUIT NO. | CIRCUIT LOAD AMPS | CIRCUIT FUSE SIZE AMPS | CIRCUIT CABLE SIZE AWG | MAINTAINING AGENCY
EX H-1 | 480 | N/A* | EX | EX | A | EX | EX | EX | ODOT
[5 empty] | B | 6.6542 | 10 | 4
[5 empty] | C | EX | EX | EX
[5 empty] | D | 11.0917 | 20 | 4
| 120 |  | 1/0
| 240 |  | 2/0
| 480 |  | 2
4