## Circuit N1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | N1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: N1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
N1-1 | N1-2 | 284 | 0.64 | 0.64 | 181.76 | 4 | 0.11 | 5.55 | 1.1562 | N1-1
N1-2 | N1-3 | 198 | 0.64 | 1.28 | 253.44 | 4 | 0.16 | 5.44 | 1.1333 | N1-2
N1-3 | N1-4 | 201 | 0.64 | 1.92 | 385.92 | 4 | 0.24 | 5.28 | 1.1 | N1-3
N1-4 | N1-5 | 222 | 0.64 | 2.56 | 568.32 | 4 | 0.35 | 5.04 | 1.05 | N1-4
N1-5 | N1-6 | 195 | 0.64 | 3.2 | 624 | 4 | 0.39 | 4.69 | 0.97708 | N1-5
N1-6 | PB-15 | 67 | 0.64 | 3.84 | 257.28 | 4 | 0.16 | 4.3 | 0.89583 | N1-6
PB-15 | N1-7 | 291 | 0 | 3.84 | 1117.44 | 4 | 0.69 | 4.14 | 0.8625 | PB-15
N1-7 | PB-14 | 673 | 3.73 | 7.57 | 5094.61 | 4 | 3.16 | 3.45 | 0.71875 | N1-7
PB-14 | CC-1 | 62 | 0 | 7.57 | 469.34 | 4 | 0.29 | 0.29 | 0.060417 | PB-14
120
240
480

## Circuit C1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | C1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 16 | 4.99
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: C1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
C1-1 | C1-2 | 169 | 0.64 | 0.64 | 108.16 | 4 | 0.07 | 7.96 | 1.6583 | C1-1
C1-2 | C1-3 | 160 | 0.64 | 1.28 | 204.8 | 4 | 0.13 | 7.89 | 1.6438 | C1-2
C1-3 | C1-4 | 210 | 0.64 | 1.92 | 403.2 | 4 | 0.25 | 7.76 | 1.6167 | C1-3
C1-4 | C1-5 | 254 | 0.64 | 2.56 | 650.24 | 4 | 0.4 | 7.51 | 1.5646 | C1-4
C1-5 | C1-6 | 592 | 0.64 | 3.2 | 1894.4 | 4 | 1.17 | 7.11 | 1.4813 | C1-5
C1-6 | C1-7 | 266 | 3.73 | 6.93 | 1843.38 | 4 | 1.14 | 5.94 | 1.2375 | C1-6
C1-7 | C1-8 | 544 | 3.73 | 10.66 | 5799.04 | 4 | 3.6 | 4.8 | 1 | C1-7
C1-8 | PB-7 | 69 | 3.73 | 14.39 | 992.91 | 4 | 0.62 | 1.2 | 0.25 | C1-8
UP-C | PB-E | 42 | 0.19 | 0.19 | 7.98 | 10 | 0.02 | 0.82 | 0.17083 | UP-C
PB-E | PB-G | 85 | 0 | 0.19 | 16.15 | 4 | 0.01 | 0.8 | 0.16667 | PB-E
UP-B | PB-G | 40 | 0.19 | 0.19 | 7.6 | 10 | 0.02 | 0.82 | 0.17083 | UP-B
PB-G | PB-D | 15 | 0 | 0.19 | 2.85 | 10 | 0.01 | 0.8 | 0.16667 | PB-G
PB-D | PB-B | 20 | 0 | 0.38 | 7.6 | 4 | 0 | 0.79 | 0.16458 | PB-D
UP-D | PB-C | 42 | 0.19 | 0.19 | 7.98 | 10 | 0.02 | 0.82 | 0.17083 | UP-D
PB-C | PB-F | 85 | 0 | 0.19 | 16.15 | 4 | 0.01 | 0.8 | 0.16667 | PB-C
UP-A | PB-F | 40 | 0.19 | 0.19 | 7.6 | 10 | 0.02 | 0.81 | 0.16875 | UP-A
PB-F | PB-B | 15 | 0 | 0.38 | 5.7 | 4 | 0 | 0.79 | 0.16458 | PB-F
PB-B | PB-A | 16 | 0 | 0.76 | 12.16 | 4 | 0.01 | 0.79 | 0.16458 | PB-B
PB-A | Disconnect | 17 | 0 | 0.76 | 12.92 | 4 | 0.01 | 0.78 | 0.1625 | PB-A
Disconnect | PB-A | 17 | 0 | 0.76 | 12.92 | 4 | 0.01 | 0.77 | 0.16042 | Disconnect
PB-A | PB-7 | 377 | 0 | 0.76 | 286.52 | 4 | 0.18 | 0.76 | 0.15833 | PB-A
PB-7 | PB-14 | 583 | 0 | 0.76 | 443.08 | 4 | 0.27 | 0.27 | 0.05625 | PB-7
PB-14 | CC-1 | 62 | 0 | 15.15 | 939.3 | 4 | 0.58 | 0.58 | 0.12083 | PB-14
120
240
480

## Circuit S1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | S1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: S1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
S1-1 | S1-2 | 250 | 0.64 | 0.64 | 160 | 4 | 0.1 | 0.1 | 0.02 | S1-1
S1-2 | S1-3 | 237 | 0.64 | 1.28 | 303.36 | 4 | 0.19 | 0.29 | 0.06 | S1-2
S1-3 | S1-4 | 237 | 0.64 | 1.92 | 455.04 | 4 | 0.28 | 0.57 | 0.12 | S1-3
S1-4 | S1-5 | 275 | 0.64 | 2.56 | 704 | 4 | 0.44 | 1.01 | 0.21 | S1-4
S1-5 | S1-6 | 236 | 0.64 | 3.2 | 755.2 | 4 | 0.47 | 1.48 | 0.31 | S1-5
S1-6 | S1-7 | 217 | 0.64 | 3.84 | 833.28 | 4 | 0.52 | 2 | 0.42 | S1-6
S1-7 | PB-1 | 191 | 0.64 | 4.48 | 855.68 | 4 | 0.53 | 2.53 | 0.53 | S1-7
S1-9 | PB-2 | 277 | 3.73 | 3.73 | 1033.21 | 4 | 0.64 | 12.23 | 2.55 | S1-9
PB-2 | PB-1 | 67 | 0 | 3.73 | 249.91 | 4 | 0.15 | 11.59 | 2.41 | PB-2
PB-1 | S1-8 | 20 | 0 | 8.21 | 164.2 | 4 | 0.1 | 11.44 | 2.38 | PB-1
S1-8 | PB-3 | 67 | 0.64 | 8.85 | 592.95 | 4 | 0.37 | 11.34 | 2.36 | S1-8
PB-3 | S1-10 | 401 | 0 | 8.85 | 3548.85 | 4 | 2.2 | 10.97 | 2.29 | PB-3
S1-10 | S1-11 | 365 | 3.73 | 12.58 | 4591.7 | 4 | 2.85 | 8.77 | 1.83 | S1-10
S1-11 | S1-12 | 327 | 3.73 | 16.31 | 5333.37 | 4 | 3.31 | 5.92 | 1.23 | S1-11
S1-12 | PB-14 | 148 | 3.73 | 20.04 | 2965.92 | 4 | 1.84 | 2.61 | 0.54 | S1-12
PB-14 | CC-1 | 62 | 0 | 20.04 | 1242.48 | 4 | 0.77 | 0.77 | 0.16 | PB-14
120
240
480

## Circuit C1 CFD CALC
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | C1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 16 | 4.99
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: C1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
C1-1 | C1-2 | 485 | 0.64 | 0.64 | 310.4 | 4 | 0.19 | 4.63 | 0.96458 | C1-1
C1-2 | C1-3 | 384 | 3.73 | 4.37 | 1678.08 | 4 | 1.04 | 4.44 | 0.925 | C1-2
C1-3 | C1-4 | 543 | 3.73 | 8.1 | 4398.3 | 4 | 2.73 | 3.4 | 0.70833 | C1-3
C1-4 | PB-6 | 69 | 3.73 | 11.83 | 816.27 | 4 | 0.51 | 0.67 | 0.13958 | C1-4
UP-C | PB-E | 28 | 0.19 | 0.19 | 5.32 | 16 | 0.05 | 0.48 | 0.1 | UP-C
PB-E | PB-D | 90 | 0 | 0.19 | 17.1 | 4 | 0.01 | 0.43 | 0.089583 | PB-E
UP-B | PB-D | 33 | 0.19 | 0.38 | 12.54 | 16 | 0.13 | 0.55 | 0.11458 | UP-B
PB-D | PB-B | 23 | 0 | 0.57 | 13.11 | 4 | 0.01 | 0.42 | 0.0875 | PB-D
UP-D | PB-C | 28 | 0.19 | 0.19 | 5.32 | 16 | 0.05 | 0.48 | 0.1 | UP-D
PB-C | PB-F | 85 | 0 | 0.19 | 16.15 | 4 | 0.01 | 0.43 | 0.089583 | PB-C
UP-A | PB-F | 28 | 0.19 | 0.76 | 21.28 | 16 | 0.21 | 0.63 | 0.13125 | UP-A
PB-F | PB-B | 10 | 0 | 0.95 | 9.5 | 4 | 0.01 | 0.42 | 0.0875 | PB-F
PB-B | PB-A | 22 | 0 | 0.95 | 20.9 | 4 | 0.01 | 0.41 | 0.085417 | PB-B
PB-A | Disconnect | 18 | 0 | 0 | 0 | 4 | 0 | 0.4 | 0.083333 | PB-A
Disconnect | PB-A | 18 | 0 | 0 | 0 | 4 | 0 | 0.4 | 0.083333 | Disconnect
PB-A | PB-6 | 415 | 0 | 0.95 | 394.25 | 4 | 0.24 | 0.4 | 0.083333 | PB-A
PB-6 | CC-1 | 20 | 0 | 12.78 | 255.6 | 4 | 0.16 | 0.16 | 0.033333 | PB-6
120
240
480

## Circuit S1 old
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | S1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: S1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
S1-1 | S1-2 | 236 | 0.64 | 0.64 | 151.04 | 4 | 0.093645 | 1.53 | 0.31875 | S1-1
S1-2 | S1-3 | 217 | 0.64 | 1.28 | 277.76 | 4 | 0.17221 | 1.44 | 0.3 | S1-2
S1-3 | S1-4 | 201 | 0.64 | 1.92 | 385.92 | 4 | 0.23927 | 1.27 | 0.26458 | S1-3
S1-5 | PB-11 | 267 | 3.73 | 3.73 | 995.91 | 4 | 0.61746 | 0.77 | 0.16042 | S1-5
PB-11 | S1-4 | 67 | 0 | 3.73 | 249.91 | 4 | 0.15494 | 0.15494 | 0.03228 | PB-11
S1-4 | PB-10 | 66.8 | 0.64 | 6.29 | 420.172 | 4 | 0.26051 | 0.26051 | 0.054272 | S1-4
PB-10 | S1-6 | 350 | 0 | 6.29 | 2201.5 | 4 | 1.3649 | 1.63 | 0.33958 | PB-10
S1-6 | S1-7 | 357 | 3.73 | 10.02 | 3577.14 | 4 | 2.2178 | 3.85 | 0.80208 | S1-6
S1-7 | S1-8 | 330 | 3.73 | 13.75 | 4537.5 | 4 | 2.8133 | 6.66 | 1.3875 | S1-7
S1-8 | PB-4 | 61.3 | 3.73 | 17.48 | 1071.524 | 4 | 0.66434 | 7.32 | 1.525 | S1-8
PB-4 | PB-5 | 82 | 0 | 17.48 | 1433.36 | 4 | 0.88868 | 8.21 | 1.7104 | PB-4
PB-5 | CC-1 | 20 | 0 | 17.48 | 349.6 | 4 | 0.21675 | 8.43 | 1.7562 | PB-5
120
240
480

## Circuit C1 old
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | C1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 16 | 4.99
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: C1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
C1-1 | PB-12 | 440 | 0.64 | 0.64 | 281.6 | 4 | 0.17459 | 2.19 | 0.45625 | C1-1
PB-12 | C1-2 | 55 | 0 | 0.64 | 35.2 | 4 | 0.021824 | 2.02 | 0.42083 | PB-12
C1-2 | PB-13 | 270 | 0.64 | 1.28 | 345.6 | 4 | 0.21427 | 2 | 0.41667 | C1-2
PB-13 | C1-3 | 124 | 0 | 1.28 | 158.72 | 4 | 0.098406 | 1.79 | 0.37292 | PB-13
C1-3 | C1-4 | 543 | 3.73 | 5.01 | 2720.43 | 4 | 1.6867 | 1.69 | 0.35208 | C1-3
UP-C | PB-E | 28 | 0.19 | 0.19 | 5.32 | 16 | 0.053094 | 0.053094 | 0.011061 | UP-C
PB-E | PB-D | 90 | 0 | 0.19 | 17.1 | 4 | 0.010602 | 0.06 | 0.0125 | PB-E
PB-D | UP-B | 28 | 0.19 | 0.38 | 10.64 | 16 | 0.10619 | 0.17 | 0.035417 | PB-D
PB-B | PB-D | 13 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | PB-B
UP-D | PB-C | 30 | 0.19 | 0.19 | 5.7 | 16 | 0.056886 | 0.056886 | 0.011851 | UP-D
PB-C | PB-B | 90 | 0 | 0.19 | 17.1 | 4 | 0.010602 | 0.07 | 0.014583 | PB-C
UP-A | PB-B | 28 | 0.19 | 0.19 | 5.32 | 16 | 0.053094 | 0.053094 | 0.011061 | UP-A
PB-B | PB-A | 22 | 0 | 0.19 | 4.18 | 4 | 0.0025916 | 0.06 | 0.0125 | PB-B
Disconnect | PB-A | 30 | 0 | 0 | 0 | 16 | 0 | 0.68 | 0.14167 | Disconnect
PB-A | PB-9 | 23 | 0 | 0 | 0 | 4 | 0 | 0.68 | 0.14167 | PB-A
PB-9 | PB-8 | 70 | 0 | 0 | 0 | 4 | 0 | 0.68 | 0.14167 | PB-9
PB-8 | C1-4 | 293 | 3.73 | 3.73 | 1092.89 | 4 | 0.67759 | 0.68 | 0.14167 | PB-8
C1-4 | PB-6 | 69 | 3.73 | 13.23 | 912.87 | 4 | 0.56598 | 5.59 | 1.1646 | C1-4
PB-6 | PB-7 | 120 | 0 | 13.23 | 1587.6 | 4 | 0.98431 | 5.02 | 1.0458 | PB-6
PB-7 | PB-2 | 176.7 | 0 | 13.23 | 2337.741 | 4 | 1.4494 | 4.04 | 0.84167 | PB-7
PB-2 | PB-3 | 101 | 0 | 13.23 | 1336.23 | 4 | 0.82846 | 2.59 | 0.53958 | PB-2
PB-3 | PB-4 | 112 | 0 | 13.23 | 1481.76 | 4 | 0.91869 | 1.76 | 0.36667 | PB-3
PB-4 | PB-5 | 82 | 0 | 13.23 | 1084.86 | 4 | 0.67261 | 0.84 | 0.175 | PB-4
PB-5 | CC-1 | 20 | 0 | 13.23 | 264.6 | 4 | 0.16405 | 0.16405 | 0.034178 | PB-5
120
240
480

## Circuit N1 old
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | N1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: N1 | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
N1-1 | N1-2 | 198 | 0.64 | 0.64 | 126.72 | 4 | 0.078566 | 4.58 | 0.95417 | N1-1
N1-2 | N1-3 | 201 | 0.64 | 1.28 | 257.28 | 4 | 0.15951 | 4.5 | 0.9375 | N1-2
N1-3 | N1-4 | 222 | 0.64 | 1.92 | 426.24 | 4 | 0.26427 | 4.34 | 0.90417 | N1-3
N1-4 | N1-5 | 195 | 0.64 | 2.56 | 499.2 | 4 | 0.3095 | 4.08 | 0.85 | N1-4
N1-5 | PB-1 | 67 | 0.64 | 3.2 | 214.4 | 4 | 0.13293 | 3.77 | 0.78542 | N1-5
PB-1 | N1-6 | 291 | 0 | 3.2 | 931.2 | 4 | 0.57734 | 3.64 | 0.75833 | PB-1
N1-6 | PB-2 | 397 | 3.73 | 6.93 | 2751.21 | 4 | 1.7058 | 3.06 | 0.6375 | N1-6
PB-2 | PB-3 | 101 | 0 | 6.93 | 699.93 | 4 | 0.43396 | 1.35 | 0.28125 | PB-2
PB-3 | PB-4 | 112 | 0 | 6.93 | 776.16 | 4 | 0.48122 | 0.92 | 0.19167 | PB-3
PB-4 | PB-5 | 82 | 0 | 6.93 | 568.26 | 4 | 0.35232 | 0.44 | 0.091667 | PB-4
PB-5 | CC-1 | 20 | 0 | 6.93 | 138.6 | 4 | 0.085932 | 0.09 | 0.01875 | PB-5
120
240
480