## Circuit N1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | ROS-23-13.06 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 220 / 480 | Circuit: | N1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 |  | Wire Factor Used (Two #4 AWG wires) 0.62 Ohms/MFT/1000 | [6 empty] | 8 | 0.78
|  |  |  | Wire Factor Used (Two #16 AWG wires) 4.99 Ohms/MFT/1000 | [6 empty] | 16 | 4.99
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
N1-1 | N1-2 | 244 | 0.64 | 0.64 | 156.16 | 4 | 0.1 | 7 | 1.4583 | N1-1
N1-2 | PB-3 | 130 | 0.64 | 1.28 | 166.4 | 4 | 0.1 | 6.9 | 1.4375 | N1-2
N1-3 | JB-C | 12 | 0.19 | 1.47 | 17.64 | 10 | 0.04 | 6.57 | 1.3687 | N1-3
JB-C | JB-B | 24 | 0 | 1.47 | 35.28 | 10 | 0.08 | 6.53 | 1.3604 | JB-C
JB-B | JB-A | 25 | 0 | 1.47 | 36.75 | 10 | 0.09 | 6.45 | 1.3438 | JB-B
JB-A | Disconnect | 20 | 0 | 1.47 | 29.4 | 10 | 0.07 | 6.36 | 1.325 | JB-A
Disconnect | PB-4 | 14 | 0 | 1.47 | 20.58 | 10 | 0.05 | 6.29 | 1.3104 | Disconnect
PB-4 | PB-3 | 27 | 0 | 1.47 | 39.69 | 4 | 0.02 | 6.24 | 1.3 | PB-4
PB-3 | PB-5 | 74 | 0 | 2.75 | 203.5 | 4 | 0.13 | 6.22 | 1.2958 | PB-3
N1-4 | JB-F | 12 | 0.19 | 2.94 | 35.28 | 10 | 0.08 | 6.8 | 1.4167 | N1-4
JB-F | JB-E | 26 | 0 | 2.94 | 76.44 | 10 | 0.18 | 6.72 | 1.4 | JB-F
JB-E | JB-D | 23 | 0 | 2.94 | 67.62 | 10 | 0.16 | 6.54 | 1.3625 | JB-E
JB-D | Disconnect | 20 | 0 | 2.94 | 58.8 | 10 | 0.14 | 6.38 | 1.3292 | JB-D
Disconnect | PB-6 | 14 | 0 | 2.94 | 41.16 | 10 | 0.1 | 6.24 | 1.3 | Disconnect
PB-6 | PB-5 | 27 | 0 | 2.94 | 79.38 | 4 | 0.05 | 6.14 | 1.2792 | PB-6
PB-5 | N1-5 | 170 | 0 | 5.69 | 967.3 | 4 | 0.6 | 6.09 | 1.2687 | PB-5
N1-5 | N1-6 | 340 | 2.8 | 8.49 | 2886.6 | 4 | 1.79 | 5.49 | 1.1438 | N1-5
N1-6 | PB-2 | 161 | 3.73 | 12.22 | 1967.42 | 4 | 1.22 | 3.7 | 0.77083 | N1-6
N1-8 | N1-7 | 434 | 3.73 | 3.73 | 1618.82 | 4 | 1 | 4.79 | 0.99792 | N1-8
N1-7 | PB-2 | 283 | 3.73 | 7.46 | 2111.18 | 4 | 1.31 | 3.79 | 0.78958 | N1-7
PB-2 | PB-1 | 131 | 0 | 19.68 | 2578.08 | 4 | 1.6 | 2.48 | 0.51667 | PB-2
PB-1 | CC-1 | 95 | 0 | 19.68 | 1869.6 | 4 | 1.16 | 0.88 | 0.18333 | PB-1
120
240
480

## Circuit S1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | ROS-23-13.06 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 220 / 480 | Circuit: | S1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 |  | Wire Factor Used (Two #4 AWG wires) 0.62 Ohms/MFT/1000 | [6 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
S1-6 | S1-7 | 448 | 3.73 | 3.73 | 1671.04 | 4 | 1.036 | 17.84 | 3.7167 | S1-6
S1-7 | S1-8 | 458 | 3.73 | 7.46 | 3416.68 | 4 | 2.1183 | 16.8 | 3.5 | S1-7
S1-8 | PB-7 | 98 | 3.73 | 11.19 | 1096.62 | 4 | 0.6799 | 14.68 | 3.0583 | S1-8
S1-1 | S1-2 | 188 | 0.64 | 11.83 | 2224.04 | 4 | 1.3789 | 12.73 | 2.6521 | S1-1
S1-2 | S1-3 | 189 | 0.64 | 12.47 | 2356.83 | 4 | 1.4612 | 11.35 | 2.3646 | S1-2
S1-3 | S1-4 | 335 | 0.64 | 13.11 | 4391.85 | 4 | 2.7229 | 9.89 | 2.0604 | S1-3
S1-4 | S1-5 | 457 | 3.73 | 16.84 | 7695.88 | 4 | 4.7714 | 7.17 | 1.4937 | S1-4
S1-5 | PB-7 | 188 | 3.73 | 20.57 | 3867.16 | 4 | 2.3976 | 2.4 | 0.5 | S1-5
PB-7 | PB-1 | 1003 | 0 | 20.57 | 20631.71 | 4 | 12.7917 | 14 | 2.9167 | PB-7
PB-1 | CC-1 | 95 | 0 | 20.57 | 1954.15 | 4 | 1.2116 | 1.21 | 0.25208 | PB-1

## not used Circuit W1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | ROS-23-13.06 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 220/480 | Circuit: | W1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 |  | Wire Factor Used (Two #4 AWG wires) 0.62 Ohms/MFT/1000 | [6 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
W1-1 | W1-2 | 287 | 3.73 | 0.29 | 83.23 | 4 | 0.051603 | 8.6146 | 1.7947 | W1-1
W1-2 | W1-3 | 448 | 3.73 | 4.02 | 1800.96 | 4 | 1.1166 | 8.563 | 1.7839 | W1-2
W1-3 | W1-4 | 458 | 3.73 | 7.75 | 3549.5 | 4 | 2.2007 | 7.4464 | 1.5513 | W1-3
W1-4 | PB-4 | 93 | 3.73 | 11.48 | 1067.64 | 4 | 0.66194 | 5.2457 | 1.0928 | W1-4
PB-4 | PB-1 | 489 | 0 | 11.48 | 5613.72 | 4 | 3.4805 | 4.5837 | 0.95494 | PB-4
PB-1 | CC-1 | 155 | 0 | 11.48 | 1779.4 | 4 | 1.1032 | 1.1032 | 0.22984 | PB-1

## not used Circuit A
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | ROS-23-13.06 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.24 | 5000V |  |  |  |  | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.235 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.48 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
A 8 | PB-8 | 67 | 0.29 | 0.29 | 19.43 | 4 | 0.0091321 | 23.6518 | 4.9275 | A 8
PB-8 | A 7 | 167 | 0 | 0.29 | 48.43 | 4 | 0.022762 | 23.6427 | 4.9256 | PB-8
A 7 | A-6 | 189 | 0.29 | 0.58 | 109.62 | 4 | 0.051521 | 23.6199 | 4.9208 | A 7
A 6 | A 5 | 790 | 4.405 | 4.985 | 3938.15 | 4 | 1.8509 | 23.5684 | 4.9101 | A 6
A 5 | A 4 | 660 | 6.1 | 11.085 | 7316.1 | 4 | 3.4386 | 21.7175 | 4.5245 | A 5
A 4 | SPLICE | 335 | 6.1 | 17.185 | 5756.975 | 4 | 2.7058 | 18.2789 | 3.8081 | A 4
4
A 1 | A 2 | 930 | 4.405 | 10.505 | 9769.65 | 4 | 4.5917 | 10.445 | 2.176 | A 1
A 2 | SPLICE | 180 | 6.1 | 16.605 | 2988.9 | 4 | 1.4048 | 5.8533 | 1.2194 | A 2
SPLICE | SPLICE | 570 | 0 | 16.605 | 9464.85 | 4 | 4.4485 | 4.4485 | 0.92677 | SPLICE
4
SPLICE | A 3 | 100 | 0 | 33.79 | 3379 | 4 | 1.5881 | 5.1281 | 1.0684 | SPLICE
A 3 | CC | 160 | 6.1 | 39.89 | 6382.4 | 4 | 2.9997 | 3.54 | 0.7375 | A 3
4
4