## COOPER
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | WOO-199-9.36 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | A | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120/240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. |  |  |  |  | Watts: | 138 | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
281-6 | 281-5 | 133 | 0.575 | 0.49 | 65.17 | 4 | 0.040405 | 1.6893 | 0.70388 | 281-6
281-5 | 199-5 | 143 | 0.575 | 1.065 | 152.295 | 4 | 0.094423 | 1.6489 | 0.68704 | 281-5
199-5 | PB-6 | 22 | 0.575 | 1.64 | 36.08 | 4 | 0.02237 | 1.5545 | 0.6477 | 199-5
PB-6 | PB-5 | 60 | 0 | 1.64 | 98.4 | 4 | 0.061008 | 1.5321 | 0.63838 | PB-6
199-4 | PB-5 | 124 | 0.575 | 2.215 | 274.66 | 4 | 0.17029 | 1.4711 | 0.61296 | 199-4
PB-5 | 281-4 | 105 | 0 | 2.215 | 232.575 | 4 | 0.1442 | 1.3008 | 0.54201 | PB-5
281-4 | 281-3 | 107 | 0.575 | 2.79 | 298.53 | 4 | 0.18509 | 1.1566 | 0.48192 | 281-4
281-3 | PB-4 | 51 | 0.575 | 3.365 | 171.615 | 4 | 0.1064 | 0.97153 | 0.4048 | 281-3
199-1 | PB-1 | 137 | 0.575 | 0.49 | 67.13 | 4 | 0.041621 | 0.86513 | 0.36047 | 199-1
199-2 | PB-1 | 155 | 0.575 | 1.065 | 165.075 | 4 | 0.10235 | 0.82351 | 0.34313 | 199-2
PB-1 | PB-2 | 58 | 0 | 1.065 | 61.77 | 4 | 0.038297 | 0.72116 | 0.30048 | PB-1
PB-2 | 199-3 | 35 | 0 | 1.065 | 37.275 | 4 | 0.02311 | 0.68286 | 0.28453 | PB-2
199-3 | 281-2 | 182 | 0.575 | 1.64 | 298.48 | 4 | 0.18506 | 0.65975 | 0.2749 | 199-3
281-2 | PB-3 | 110 | 0.575 | 2.215 | 243.65 | 4 | 0.15106 | 0.47469 | 0.19779 | 281-2
281-1 | PB-3 | 93 | 0.575 | 2.79 | 259.47 | 4 | 0.16087 | 0.32363 | 0.13485 | 281-1
PB-3 | PB-4 | 61 | 0 | 2.79 | 170.19 | 4 | 0.10552 | 0.16276 | 0.067816 | PB-3
PB-4 | CC-1 | 15 | 0 | 6.155 | 92.325 | 4 | 0.057242 | 0.057242 | 0.023851 | PB-4
120
240
480

## GE
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | WOO-199-9.36 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | A | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120/240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. |  |  |  |  | Watts: | 136 | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
281-6 | 281-5 | 133 | 0.56667 | 0.49 | 65.17 | 4 | 0.040405 | 1.6719 | 0.69662 | 281-6
281-5 | 199-5 | 143 | 0.56667 | 1.0567 | 151.1033 | 4 | 0.093684 | 1.6315 | 0.67979 | 281-5
199-5 | PB-6 | 22 | 0.56667 | 1.6233 | 35.7133 | 4 | 0.022142 | 1.5378 | 0.64075 | 199-5
PB-6 | PB-5 | 60 | 0 | 1.6233 | 97.4 | 4 | 0.060388 | 1.5157 | 0.63153 | PB-6
199-4 | PB-5 | 124 | 0.56667 | 2.19 | 271.56 | 4 | 0.16837 | 1.4553 | 0.60637 | 199-4
PB-5 | 281-4 | 105 | 0 | 2.19 | 229.95 | 4 | 0.14257 | 1.2869 | 0.53621 | PB-5
281-4 | 281-3 | 107 | 0.56667 | 2.7567 | 294.9633 | 4 | 0.18288 | 1.1443 | 0.47681 | 281-4
281-3 | PB-4 | 51 | 0.56667 | 3.3233 | 169.49 | 4 | 0.10508 | 0.96146 | 0.40061 | 281-3
199-1 | PB-1 | 137 | 0.56667 | 0.49 | 67.13 | 4 | 0.041621 | 0.85638 | 0.35682 | 199-1
199-2 | PB-1 | 155 | 0.56667 | 1.0567 | 163.7833 | 4 | 0.10155 | 0.81476 | 0.33948 | 199-2
PB-1 | PB-2 | 58 | 0 | 1.0567 | 61.2867 | 4 | 0.037998 | 0.71321 | 0.29717 | PB-1
PB-2 | 199-3 | 35 | 0 | 1.0567 | 36.9833 | 4 | 0.02293 | 0.67522 | 0.28134 | PB-2
199-3 | 281-2 | 182 | 0.56667 | 1.6233 | 295.4467 | 4 | 0.18318 | 0.65229 | 0.27179 | 199-3
281-2 | PB-3 | 110 | 0.56667 | 2.19 | 240.9 | 4 | 0.14936 | 0.46911 | 0.19546 | 281-2
281-1 | PB-3 | 93 | 0.56667 | 2.7567 | 256.37 | 4 | 0.15895 | 0.31975 | 0.13323 | 281-1
PB-3 | PB-4 | 61 | 0 | 2.7567 | 168.1567 | 4 | 0.10426 | 0.1608 | 0.067 | PB-3
PB-4 | CC-1 | 15 | 0 | 6.08 | 91.2 | 4 | 0.056544 | 0.056544 | 0.02356 | PB-4
120
240
480

## AEL
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | WOO-199-9.36 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | A | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120/240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. |  |  |  |  | Watts: | 118 | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
281-6 | 281-5 | 133 | 0.49167 | 0.49 | 65.17 | 4 | 0.040405 | 1.5152 | 0.63133 | 281-6
281-5 | 199-5 | 143 | 0.49167 | 0.98167 | 140.3783 | 4 | 0.087035 | 1.4748 | 0.61449 | 281-5
199-5 | PB-6 | 22 | 0.49167 | 1.4733 | 32.4133 | 4 | 0.020096 | 1.3878 | 0.57823 | 199-5
PB-6 | PB-5 | 60 | 0 | 1.4733 | 88.4 | 4 | 0.054808 | 1.3677 | 0.56986 | PB-6
199-4 | PB-5 | 124 | 0.49167 | 1.965 | 243.66 | 4 | 0.15107 | 1.3128 | 0.54702 | 199-4
PB-5 | 281-4 | 105 | 0 | 1.965 | 206.325 | 4 | 0.12792 | 1.1618 | 0.48407 | PB-5
281-4 | 281-3 | 107 | 0.49167 | 2.4567 | 262.8633 | 4 | 0.16298 | 1.0339 | 0.43077 | 281-4
281-3 | PB-4 | 51 | 0.49167 | 2.9483 | 150.365 | 4 | 0.093226 | 0.87088 | 0.36287 | 281-3
199-1 | PB-1 | 137 | 0.49167 | 0.49 | 67.13 | 4 | 0.041621 | 0.77765 | 0.32402 | 199-1
199-2 | PB-1 | 155 | 0.49167 | 0.98167 | 152.1583 | 4 | 0.094338 | 0.73603 | 0.30668 | 199-2
PB-1 | PB-2 | 58 | 0 | 0.98167 | 56.9367 | 4 | 0.035301 | 0.6417 | 0.26737 | PB-1
PB-2 | 199-3 | 35 | 0 | 0.98167 | 34.3583 | 4 | 0.021302 | 0.6064 | 0.25266 | PB-2
199-3 | 281-2 | 182 | 0.49167 | 1.4733 | 268.1467 | 4 | 0.16625 | 0.58509 | 0.24379 | 199-3
281-2 | PB-3 | 110 | 0.49167 | 1.965 | 216.15 | 4 | 0.13401 | 0.41884 | 0.17452 | 281-2
281-1 | PB-3 | 93 | 0.49167 | 2.4567 | 228.47 | 4 | 0.14165 | 0.28483 | 0.11868 | 281-1
PB-3 | PB-4 | 61 | 0 | 2.4567 | 149.8567 | 4 | 0.092911 | 0.14318 | 0.059657 | PB-3
PB-4 | CC-1 | 15 | 0 | 5.405 | 81.075 | 4 | 0.050266 | 0.050266 | 0.020944 | PB-4
120
240
480