## Circuit EB
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | CUY-90 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | EB | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 2 | AWG. | 0.19 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
EB13 | EB12 | 601 | 6.6667 | 6.6667 | 4006.6667 | 2 | 1.5225 | 21.1885 | 4.4143
EB12 | EB11 | 479 | 6.6667 | 13.3333 | 6386.6667 | 2 | 2.4269 | 19.6659
EB11 | EB10 | 200 | 0.89583 | 14.2292 | 2845.8333 | 2 | 1.0814 | 17.239
EB10 | EB9 | 290 | 0.89583 | 15.125 | 4386.25 | 2 | 1.6668 | 16.1576
EB9 | EB8 | 300 | 0.89583 | 16.0208 | 4806.25 | 2 | 1.8264 | 14.4908
EB8 | EB7 | 400 | 0.89583 | 16.9167 | 6766.6667 | 2 | 2.5713 | 12.6644
EB7 | EB6 | 567 | 6.6667 | 23.5833 | 13371.75 | 2 | 5.0813 | 10.0931
EB6 | LCC "E" | 436 | 6.6667 | 30.25 | 13189 | 2 | 5.0118 | 5.0118
120
240
480

## example
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | MED-224-13.47 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 120 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
AA5 | AA4 | 121 | 0.75 | 0.75 | 90.75 | 4 | 0.056265 | 0.83937 | 0.69947 | AA5
AA4 | PB8 | 510 | 0.75 | 1.5 | 765 | 4 | 0.4743 | 0.7831 | 0.65259
PB8 | AA3 | 65 | 0 | 1.5 | 97.5 | 4 | 0.06045 | 0.3088 | 0.25734
AA3 | PB4 | 31 | 0.75 | 2.25 | 69.75 | 4 | 0.043245 | 0.24835 | 0.20696
AA1 | PB18 | 18 | 0.75 | 3 | 54 | 4 | 0.03348 |  | 0
PB18 | PB14 | 30 | 0
AA2 | PB14 | 15 | 0.75 | 3.75 | 56.25 | 4 | 0.034875 |  | 0
PB14 | LCC | 79 |  | 3.75 | 296.25 | 4 | 0.18368 | 0.18
120
240
480