## Circuit BW1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | SUM-8-1.75 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | BW | Circuit: | BW1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'BW1' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
BW1-11 | BW1-10 | 166 | 0.68 | 0.68 | 112.88 | 4 | 0.069986 | 1.9777 | 0.41203 | BW1-11
BW1-10 | BW1-9 | 160 | 0.68 | 1.36 | 217.6 | 4 | 0.13491 | 1.9077 | 0.39745 | BW1-10
BW1-9 | BW1-8 | 163 | 0.68 | 2.04 | 332.52 | 4 | 0.20616 | 1.7728 | 0.36934 | BW1-9
BW1-8 | BW1-7 | 157 | 0.68 | 2.72 | 427.04 | 4 | 0.26476 | 1.5667 | 0.32639 | BW1-8
BW1-7 | PB-1 | 138 | 0.68 | 3.4 | 469.2 | 4 | 0.2909 | 1.3019 | 0.27123 | BW1-7
BW1-6 | BW1-5 | 160 | 0.34 | 0.34 | 54.4 | 4 | 0.033728 | 1.3742 | 0.28629 | BW1-6
BW1-5 | BW1-4 | 162 | 0.34 | 0.68 | 110.16 | 4 | 0.068299 | 1.3405 | 0.27927 | BW1-5
BW1-4 | BW1-3 | 161 | 0.34 | 1.02 | 164.22 | 4 | 0.10182 | 1.2722 | 0.26504 | BW1-4
BW1-3 | BW1-2 | 159 | 0.34 | 1.36 | 216.24 | 4 | 0.13407 | 1.1704 | 0.24383 | BW1-3
BW1-2 | PB-1 | 24 | 0.34 | 1.7 | 40.8 | 4 | 0.025296 | 1.0363 | 0.21589 | BW1-2
PB-1 | BW1-1 | 148 | 0 | 5.1 | 754.8 | 4 | 0.46798 | 1.011 | 0.21062 | PB-1
BW1-1 | PS 'BW' | 161 | 0.34 | 5.44 | 875.84 | 4 | 0.54302 | 0.54302 | 0.11313 | BW1-1
120
240
480

## Circuit BW2
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | SUM-8-1.75 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | BW | Circuit: | BW2 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'BW2' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
BW2-15 | BW2-14 | 157 | 0.34 | 0.34 | 53.38 | 4 | 0.033096 | 4.0861 | 0.85128 | BW2-15
BW2-14 | BW2-13 | 157 | 0.34 | 0.68 | 106.76 | 4 | 0.066191 | 4.0531 | 0.84439 | BW2-14
BW2-13 | BW2-12 | 157 | 0.34 | 1.02 | 160.14 | 4 | 0.099287 | 3.9869 | 0.8306 | BW2-13
BW2-12 | BW2-11 | 155 | 0.34 | 1.36 | 210.8 | 4 | 0.1307 | 3.8876 | 0.80991 | BW2-12
BW2-11 | BW2-10 | 160 | 0.34 | 1.7 | 272 | 4 | 0.16864 | 3.7569 | 0.78268 | BW2-11
BW2-10 | BW2-9 | 160 | 0.34 | 2.04 | 326.4 | 4 | 0.20237 | 3.5882 | 0.74755 | BW2-10
BW2-9 | BW2-8 | 160 | 0.34 | 2.38 | 380.8 | 4 | 0.2361 | 3.3859 | 0.70539 | BW2-9
BW2-8 | BW2-7 | 160 | 0.34 | 2.72 | 435.2 | 4 | 0.26982 | 3.1498 | 0.6562 | BW2-8
BW2-7 | BW2-6 | 160 | 0.34 | 3.06 | 489.6 | 4 | 0.30355 | 2.8799 | 0.59999 | BW2-7
BW2-6 | BW2-5 | 159 | 0.34 | 3.4 | 540.6 | 4 | 0.33517 | 2.5764 | 0.53675 | BW2-6
BW2-5 | BW2-4 | 159 | 0.34 | 3.74 | 594.66 | 4 | 0.36869 | 2.2412 | 0.46692 | BW2-5
BW2-4 | BW2-3 | 160 | 0.34 | 4.08 | 652.8 | 4 | 0.40474 | 1.8725 | 0.39011 | BW2-4
BW2-3 | BW2-2 | 159 | 0.34 | 4.42 | 702.78 | 4 | 0.43572 | 1.4678 | 0.30579 | BW2-3
BW2-2 | BW2-1 | 159 | 0.34 | 4.76 | 756.84 | 4 | 0.46924 | 1.0321 | 0.21502 | BW2-2
BW2-1 | PS - 'BW' | 178 | 0.34 | 5.1 | 907.8 | 4 | 0.56284 | 0.56284 | 0.11726 | BW2-1
120
240
480

## Circuit BE1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | SUM-8-1.75 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | BE | Circuit: | BE1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'BE1' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
BE1-6 | BE1-5 | 142 | 0.34 | 0.34 | 48.28 | 4 | 0.029934 | 0.6773 | 0.1411 | BE1-6
BE1-5 | BE1-4 | 161 | 0.34 | 0.68 | 109.48 | 4 | 0.067878 | 0.64737 | 0.13487 | BE1-5
BE1-4 | BE1-3 | 160 | 0.34 | 1.02 | 163.2 | 4 | 0.10118 | 0.57949 | 0.12073 | BE1-4
BE1-3 | BE1-2 | 162 | 0.34 | 1.36 | 220.32 | 4 | 0.1366 | 0.47831 | 0.099647 | BE1-3
BE1-2 | BE1-1 | 155 | 0.34 | 1.7 | 263.5 | 4 | 0.16337 | 0.34171 | 0.071189 | BE1-2
BE1-1 | PS - 'BE' | 141 | 0.34 | 2.04 | 287.64 | 4 | 0.17834 | 0.17834 | 0.037153 | BE1-1
120
240
480

## Circuit BWE2
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | SUM-8-1.75 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | BE | Circuit: | BE2 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'BE2' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
BE2-15 | BE2-14 | 159 | 0.34 | 0.34 | 54.06 | 4 | 0.033517 | 3.7919 | 0.78997 | BE2-15
BE2-14 | BE2-13 | 161 | 0.34 | 0.68 | 109.48 | 4 | 0.067878 | 3.7584 | 0.78299 | BE2-14
BE2-13 | BE2-12 | 160 | 0.34 | 1.02 | 163.2 | 4 | 0.10118 | 3.6905 | 0.76885 | BE2-13
BE2-12 | BE2-11 | 160 | 0.34 | 1.36 | 217.6 | 4 | 0.13491 | 3.5893 | 0.74777 | BE2-12
BE2-11 | BE2-10 | 159 | 0.34 | 1.7 | 270.3 | 4 | 0.16759 | 3.4544 | 0.71966 | BE2-11
BE2-10 | BE2-9 | 155 | 0.34 | 2.04 | 316.2 | 4 | 0.19604 | 3.2868 | 0.68475 | BE2-10
BE2-9 | BE2-8 | 160 | 0.34 | 2.38 | 380.8 | 4 | 0.2361 | 3.0907 | 0.64391 | BE2-9
BE2-8 | BE2-7 | 160 | 0.34 | 2.72 | 435.2 | 4 | 0.26982 | 2.8547 | 0.59472 | BE2-8
BE2-7 | BE2-6 | 160 | 0.34 | 3.06 | 489.6 | 4 | 0.30355 | 2.5848 | 0.53851 | BE2-7
BE2-6 | BE2-5 | 160 | 0.34 | 3.4 | 544 | 4 | 0.33728 | 2.2813 | 0.47527 | BE2-6
BE2-5 | BE2-4 | 159 | 0.34 | 3.74 | 594.66 | 4 | 0.36869 | 1.944 | 0.405 | BE2-5
BE2-4 | BE2-3 | 160 | 0.34 | 4.08 | 652.8 | 4 | 0.40474 | 1.5753 | 0.32819 | BE2-4
BE2-3 | BE2-2 | 159 | 0.34 | 4.42 | 702.78 | 4 | 0.43572 | 1.1706 | 0.24387 | BE2-3
BE2-2 | BE2-1 | 159 | 0.34 | 4.76 | 756.84 | 4 | 0.46924 | 0.73485 | 0.15309 | BE2-2
BE2-1 | PS - 'BE' | 84 | 0.34 | 5.1 | 428.4 | 4 | 0.26561 | 0.26561 | 0.055335 | BE2-1
120
240
480

## Circuit SB1
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | FRA-71-14.36 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  |  | Circuit: | 810 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'SB1' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
LP1 | LP2 | 111 | 0.14 | 0.14 | 15.54 | 4 | 0.0096348 | 2.4067 | 0.5014 | LP1
LP2 | LP3 | 103 | 0.14 | 0.28 | 28.84 | 4 | 0.017881 | 2.3971 | 0.49939 | LP2
LP3 | LP4 | 146 | 0.14 | 0.42 | 61.32 | 4 | 0.038018 | 2.3792 | 0.49566 | LP3
LP4 | LP5 | 145 | 0.14 | 0.56 | 81.2 | 4 | 0.050344 | 2.3412 | 0.48774 | LP4
LP5 | LP6 | 149 | 0.14 | 0.7 | 104.3 | 4 | 0.064666 | 2.2908 | 0.47726 | LP5
LP6 | LP7 | 139 | 0.14 | 0.84 | 116.76 | 4 | 0.072391 | 2.2262 | 0.46378 | LP6
LP7 | PB1 | 93 | 0.14 | 0.98 | 91.14 | 4 | 0.056507 | 2.1538 | 0.4487 | LP7
LP8 | LP9 | 131 | 0.14 | 0.14 | 18.34 | 4 | 0.011371 | 2.1239 | 0.44248 | LP8
LP9 | PB1 | 88 | 0.14 | 0.28 | 24.64 | 4 | 0.015277 | 2.1125 | 0.44011 | LP9
PB1 | PB2 | 103 | 0 | 1.26 | 129.78 | 4 | 0.080464 | 2.0973 | 0.43693 | PB1
L1 | PB2 | 21 | 0.2 | 0.2 | 4.2 | 4 | 0.002604 | 2.0194 | 0.42071 | L1
PB2 | L2 | 79 | 0 | 1.46 | 115.34 | 4 | 0.071511 | 2.0168 | 0.42017 | PB2
L2 | PB3 | 97 | 0.2 | 1.66 | 161.02 | 4 | 0.099832 | 1.9453 | 0.40527 | L2
WP1 | PB3 | 30 | 0.5 | 0.5 | 15 | 4 | 0.0093 | 1.8548 | 0.38641 | WP1
PB3 | L3 | 48 | 0 | 2.16 | 103.68 | 4 | 0.064282 | 1.8455 | 0.38447 | PB3
L3 | PB4 | 79 | 0.2 | 2.36 | 186.44 | 4 | 0.11559 | 1.7812 | 0.37108 | L3
WP2 | PB4 | 27 | 0.5 | 0.5 | 13.5 | 4 | 0.00837 | 1.674 | 0.34874 | WP2
PB4 | L4 | 33 | 0 | 2.86 | 94.38 | 4 | 0.058516 | 1.6656 | 0.347 | PB4
L4 | L5 | 120 | 0.2 | 3.06 | 367.2 | 4 | 0.22766 | 1.6071 | 0.33481 | L4
L5 | L6 | 103 | 0.2 | 3.26 | 335.78 | 4 | 0.20818 | 1.3794 | 0.28738 | L5
L6 | PB5 | 45 | 0.2 | 3.46 | 155.7 | 4 | 0.096534 | 1.1712 | 0.244 | L6
L7 | PB5 | 73 | 0.2 | 0.2 | 14.6 | 4 | 0.009052 | 1.0837 | 0.22578 | L7
PB5 | L8 | 94 | 0 | 3.66 | 344.04 | 4 | 0.2133 | 1.0747 | 0.22389 | PB5
L8 | PB6 | 78 | 0.2 | 3.86 | 301.08 | 4 | 0.18667 | 0.86138 | 0.17945 | L8
L11 | L10 | 105 | 0.2 | 0.2 | 21 | 4 | 0.01302 | 0.72654 | 0.15136 | L11
L10 | L9 | 113 | 0.2 | 0.4 | 45.2 | 4 | 0.028024 | 0.71352 | 0.14865 | L10
L9 | PB6 | 29 | 0.2 | 0.6 | 17.4 | 4 | 0.010788 | 0.6855 | 0.14281 | L9
PB6 | CC | 244 | 0 | 4.46 | 1088.24 | 4 | 0.67471 | 0.67471 | 0.14056 | PB6
120
240
480