## Circuit MI
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | FRA-71-14.36 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | M | Circuit: | MI | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'MI' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
MI-25 | MI-24 | 177 | 0.28 | 0.28 | 49.56 | 4 | 0.030727 | 10.0566 | 2.0951 | MI-25
MI-24 | MI-23 | 176 | 0.28 | 0.56 | 98.56 | 4 | 0.061107 | 10.0259 | 2.0887 | MI-24
MI-23 | MI-22 | 176 | 0.28 | 0.84 | 147.84 | 4 | 0.091661 | 9.9648 | 2.076 | MI-23
MI-22 | MI-21 | 177 | 0.28 | 1.12 | 198.24 | 4 | 0.12291 | 9.8732 | 2.0569 | MI-22
MI-21 | MI-20 | 176 | 0.28 | 1.4 | 246.4 | 4 | 0.15277 | 9.7502 | 2.0313 | MI-21
MI-20 | MI-19 | 176 | 0.28 | 1.68 | 295.68 | 4 | 0.18332 | 9.5975 | 1.9995 | MI-20
MI-19 | MI-18 | 170 | 0.28 | 1.96 | 333.2 | 4 | 0.20658 | 9.4142 | 1.9613 | MI-19
MI-18 | MI-17 | 180 | 0.28 | 2.24 | 403.2 | 4 | 0.24998 | 9.2076 | 1.9182 | MI-18
MI-17 | MI-16 | 180 | 0.28 | 2.52 | 453.6 | 4 | 0.28123 | 8.9576 | 1.8662 | MI-17
MI-16 | MI-15 | 180 | 0.28 | 2.8 | 504 | 4 | 0.31248 | 8.6764 | 1.8076 | MI-16
MI-15 | MI-14 | 180 | 0.28 | 3.08 | 554.4 | 4 | 0.34373 | 8.3639 | 1.7425 | MI-15
MI-14 | MI-13 | 182 | 0.28 | 3.36 | 611.52 | 4 | 0.37914 | 8.0201 | 1.6709 | MI-14
MI-13 | MI-12 | 178 | 0.28 | 3.64 | 647.92 | 4 | 0.40171 | 7.641 | 1.5919 | MI-13
MI-12 | MI-11 | 180 | 0.28 | 3.92 | 705.6 | 4 | 0.43747 | 7.2393 | 1.5082 | MI-12
MI-11 | MI-10 | 177 | 0.28 | 4.2 | 743.4 | 4 | 0.46091 | 6.8018 | 1.417 | MI-11
MI-10 | MI-9 | 180 | 0.28 | 4.48 | 806.4 | 4 | 0.49997 | 6.3409 | 1.321 | MI-10
MI-9 | MI-8 | 180 | 0.28 | 4.76 | 856.8 | 4 | 0.53122 | 5.8409 | 1.2169 | MI-9
MI-8 | MI-7 | 178 | 0.28 | 5.04 | 897.12 | 4 | 0.55621 | 5.3097 | 1.1062 | MI-8
MI-7 | MI-6 | 179 | 0.28 | 5.32 | 952.28 | 4 | 0.59041 | 4.7535 | 0.99032 | MI-7
MI-6 | MI-5 | 178 | 0.28 | 5.6 | 996.8 | 4 | 0.61802 | 4.1631 | 0.86731 | MI-6
MI-5 | MI-4 | 178 | 0.28 | 5.88 | 1046.64 | 4 | 0.64892 | 3.5451 | 0.73856 | MI-5
MI-4 | MI-3 | 236 | 0.28 | 6.16 | 1453.76 | 4 | 0.90133 | 2.8962 | 0.60337 | MI-4
MI-3 | MI-2 | 159 | 0.28 | 6.44 | 1023.96 | 4 | 0.63486 | 1.9948 | 0.41559 | MI-3
MI-2 | MI-1 | 166 | 0.28 | 6.72 | 1115.52 | 4 | 0.69162 | 1.36 | 0.28333 | MI-2
MI-1 | PS - 'M' | 154 | 0.28 | 7 | 1078 | 4 | 0.66836 | 0.66836 | 0.13924 | MI-1
120
240
480

## Circuit MJ
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | FRA-71-14.36 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | M | Circuit: | MJ | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'MJ' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
MJ-9 | MJ-8 | 190 | 0.44 | 0.44 | 83.6 | 4 | 0.051832 | 1.3543 | 0.28214 | MJ-9
MJ-8 | MJ-7 | 200 | 0.44 | 0.88 | 176 | 4 | 0.10912 | 1.3025 | 0.27135 | MJ-8
MJ-7 | MJ-6 | 131 | 0.44 | 1.32 | 172.92 | 4 | 0.10721 | 1.1933 | 0.24861 | MJ-7
MJ-6 | MJ-5 | 82 | 0.28 | 1.6 | 131.2 | 4 | 0.081344 | 1.0861 | 0.22628 | MJ-6
MJ-5 | MJ-4 | 59 | 0.06 | 1.66 | 97.94 | 4 | 0.060723 | 1.0048 | 0.20933 | MJ-5
MJ-4 | MJ-3 | 60 | 0.06 | 1.72 | 103.2 | 4 | 0.063984 | 0.94406 | 0.19668 | MJ-4
MJ-3 | MJ-2 | 98 | 0.06 | 1.78 | 174.44 | 4 | 0.10815 | 0.88008 | 0.18335 | MJ-3
MJ-2 | MJ-1 | 83 | 0.28 | 2.06 | 170.98 | 4 | 0.10601 | 0.77192 | 0.16082 | MJ-2
MJ-1 | CC-'M' | 459 | 0.28 | 2.34 | 1074.06 | 4 | 0.66592 | 0.66592 | 0.13873 | MJ-1
120
240
480