## Circuit A
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | PRE-70 WB TRUCK PARKING |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 240 | Circuit: | A1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120/240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'A1' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
A14 | A13 | 246 | 0.72917 | 0.72917 | 179.375 | 4 | 0.11121 | 12.6779 | 2.6412 | A14
A13 | A12 | 246 | 0.72917 | 1.4583 | 358.75 | 4 | 0.22243 | 12.5667 | 2.6181 | A13
A12 | A11 | 246 | 0.72917 | 2.1875 | 538.125 | 4 | 0.33364 | 12.3442 | 2.5717 | A12
A11 | A10 | 246 | 0.72917 | 2.9167 | 717.5 | 4 | 0.44485 | 12.0106 | 2.5022 | A11
A10 | A9 | 245 | 0.72917 | 3.6458 | 893.2292 | 4 | 0.5538 | 11.5658 | 2.4095 | A10
A9 | A8 | 246 | 0.72917 | 4.375 | 1076.25 | 4 | 0.66727 | 11.0119 | 2.2942 | A9
A8 | A7 | 246 | 0.72917 | 5.1042 | 1255.625 | 4 | 0.77849 | 10.3447 | 2.1551 | A8
A7 | A6 | 245 | 0.72917 | 5.8333 | 1429.1667 | 4 | 0.88608 | 9.5662 | 1.993 | A7
A6 | A5 | 248 | 0.72917 | 6.5625 | 1627.5 | 4 | 1.0091 | 8.6801 | 1.8084 | A6
A5 | A4 | 220 | 0.72917 | 7.2917 | 1604.1667 | 4 | 0.99458 | 7.6711 | 1.5981 | A5
A4 | PB-4 | 48 | 0.72917 | 8.0208 | 385 | 4 | 0.2387 | 6.6765 | 1.3909 | A4
A3 | A2 | 295 | 4.9167 | 4.9167 | 1450.4167 | 4 | 0.89926 | 11.3944 | 2.3738 | A3
A2 | A1 | 301 | 4.9167 | 9.8333 | 2959.8333 | 4 | 1.8351 | 10.4951 | 2.1865 | A2
A1 | PB-5 | 188 | 4.9167 | 14.75 | 2773 | 4 | 1.7193 | 8.66 | 1.8042 | A1
PB-5 | PB-4 | 55 | 0 | 14.75 | 811.25 | 4 | 0.50298 | 6.9407 | 1.446 | PB-5
PB-4 | PB-3 | 260 | 0 | 22.7708 | 5920.4167 | 4 | 3.6707 | 6.4378 | 1.3412 | PB-4
PB-3 | PB-2 | 47 | 0 | 22.7708 | 1070.2292 | 4 | 0.66354 | 2.7671 | 0.57648 | PB-3
PB-2 | PB-1 | 124 | 0 | 22.7708 | 2823.5833 | 4 | 1.7506 | 2.1036 | 0.43824 | PB-2
PB-1 | CC-1 | 25 | 0 | 22.7708 | 569.2708 | 4 | 0.35295 | 0.35295 | 0.073531 | PB-1
|  | TOTAL AMPS: | 22.7708 |  |  |  |  | MAX % DROP: | 2.6412
120
240
480

## Circuit B
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | PRE-70 WB TRUCK PARKING |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 240 | Circuit: | B1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120/240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'B1' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
B14 | B13 | 246 | 0.72917 | 0.72917 | 179.375 | 4 | 0.11121 | 15.2764 | 3.1826 | B14
B13 | B12 | 246 | 0.72917 | 1.4583 | 358.75 | 4 | 0.22243 | 15.1651 | 3.1594 | B13
B12 | B11 | 246 | 0.72917 | 2.1875 | 538.125 | 4 | 0.33364 | 14.9427 | 3.1131 | B12
B11 | B10 | 246 | 0.72917 | 2.9167 | 717.5 | 4 | 0.44485 | 14.6091 | 3.0436 | B11
B10 | B9 | 245 | 0.72917 | 3.6458 | 893.2292 | 4 | 0.5538 | 14.1642 | 2.9509 | B10
B9 | B8 | 246 | 0.72917 | 4.375 | 1076.25 | 4 | 0.66727 | 13.6104 | 2.8355 | B9
B8 | B7 | 246 | 0.72917 | 5.1042 | 1255.625 | 4 | 0.77849 | 12.9432 | 2.6965 | B8
B7 | PB-7 | 245 | 0.72917 | 5.8333 | 1429.1667 | 4 | 0.88608 | 12.1647 | 2.5343 | B7
PB-7 | PB-6 | 248 | 0 | 5.8333 | 1446.6667 | 4 | 0.89693 | 11.2786 | 2.3497 | PB-7
B6 | B5 | 220 | 0.72917 | 0.72917 | 160.4167 | 4 | 0.099458 | 10.9246 | 2.276 | B6
B5 | B4 | 48 | 0.72917 | 1.4583 | 70 | 4 | 0.0434 | 10.8251 | 2.2552 | B5
B4 | PB-6 | 295 | 0.72917 | 2.1875 | 645.3125 | 4 | 0.40009 | 10.7817 | 2.2462 | B4
PB-6 | B3 | 301 | 0 | 8.0208 | 2414.2708 | 4 | 1.4968 | 10.3817 | 2.1628 | PB-6
B3 | B2 | 188 | 7.375 | 15.3958 | 2894.4167 | 4 | 1.7945 | 8.8848 | 1.851 | B3
B2 | B1 | 55 | 4.9167 | 20.3125 | 1117.1875 | 4 | 0.69266 | 7.0903 | 1.4771 | B2
B1 | PB-2 | 260 | 4.9167 | 25.2292 | 6559.5833 | 4 | 4.0669 | 6.3976 | 1.3328 | B1
PB-2 | PB-1 | 124 | 0 | 25.2292 | 3128.4167 | 4 | 1.9396 | 2.3307 | 0.48556 | PB-2
PB-1 | CC-1 | 25 | 0 | 25.2292 | 630.7292 | 4 | 0.39105 | 0.39105 | 0.081469 | PB-1
|  | TOTAL AMPS: | 25.2292 |  |  |  |  | MAX % DROP: | 3.1826
120
240
480

## Circuit C
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | PRE-70 WB TRUCK PARKING |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 240 | Circuit: | C1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120/240 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'C1' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
C9 | C8 | 220 | 4.9167 | 4.9167 | 1081.6667 | 4 | 0.67063 | 22.4967 | 4.6868 | C9
C8 | C7 | 48 | 4.9167 | 9.8333 | 472 | 4 | 0.29264 | 21.826 | 4.5471 | C8
C7 | PB-11 | 295 | 4.9167 | 14.75 | 4351.25 | 4 | 2.6978 | 21.5334 | 4.4861 | C7
PB-11 | PB-10 | 301 | 0 | 14.75 | 4439.75 | 4 | 2.7526 | 18.8356 | 3.9241 | PB-11
C6 | C5 | 220 | 4.9167 | 4.9167 | 1081.6667 | 4 | 0.67063 | 20.2668 | 4.2223 | C6
C5 | C4 | 48 | 7.375 | 12.2917 | 590 | 4 | 0.3658 | 19.5962 | 4.0825 | C5
C4 | PB-10 | 295 | 4.9167 | 17.2083 | 5076.4583 | 4 | 3.1474 | 19.2304 | 4.0063 | C4
PB-10 | C3 | 301 | 0 | 31.9583 | 9619.4583 | 4 | 5.9641 | 16.083 | 3.3506 | PB-10
C3 | PB-9 | 188 | 0.72917 | 32.6875 | 6145.25 | 4 | 3.8101 | 10.1189 | 2.1081 | C3
PB-9 | PB-8 | 55 | 0 | 32.6875 | 1797.8125 | 4 | 1.1146 | 6.3088 | 1.3143 | PB-9
C2 | PB-8 | 260 | 0.72917 | 0.72917 | 189.5833 | 4 | 0.11754 | 5.3117 | 1.1066 | C2
PB-8 | PB-1 | 124 | 0 | 33.4167 | 4143.6667 | 4 | 2.5691 | 5.1942 | 1.0821 | PB-8
C1 | PB-1 | 260 | 0.72917 | 0.72917 | 189.5833 | 4 | 0.11754 | 2.7427 | 0.57139 | C1
PB-1 | CC-1 | 124 | 0 | 34.1458 | 4234.0833 | 4 | 2.6251 | 2.6251 | 0.5469 | PB-1
|  | TOTAL AMPS: | 34.1458 |  |  |  |  | MAX % DROP: | 4.6868
120
240
480

## CONTROL CENTER DATA TABLE
CONTROL CENTER DATA
CONTROL CENTER DESIGNATION | LINE VOLTS | CONNECTED LOAD (KVA) | SERVICE ENTRANCE CONDUCTOR SIZE - AWG | ENCLOSURE RATING (AMPS) | CIRCUIT NO. | CIRCUIT LOAD AMPS | CIRCUIT FUSE SIZE AMPS | CIRCUIT CABLE SIZE AWG | MAINTAINING AGENCY
CC-1 (LIGHTING) | 240 | 19.715 | 1/0 | 200 | A1 | 22.7708 | 30 | 4 | ODOT
[5 empty] | B1 | 25.2292 | 40 | 4
[5 empty] | C1 | 34.1458 | 50 | 4
- | - | - | - | - | - | - | - | - | -
[5 empty] | - | - | - | -
[5 empty] | - | - | - | -
| 120 |  | 1/0
| 240 |  | 2/0
| 480 |  | 2
4