## CC-1
VOLTAGE DROP CALCULATIONS - SR 117 AND SR 501/S WAPAK ROAD
VOLTAGE:240
OHMS/FT/1000 FROM TEM-FIGURE 1198-12
| WIRE FACTOR USED (THREE - NO. 4 AWG WIRES) | [7 empty] | 0.62 | 2*Wire Resistance (2*0.31)
[6 empty] | WATTS | VOLTS | LAMP LOSS
| LIGHT FIXTURE (WORST CASE WATTAGE OF THE 2 FIXTURES) |  |  |  |  | 135 | 240 | 1 | = | 0.5625 | AMPS/FIXTURE
VOLTAGE DROP IN A SECTION = AMPS IN AND BEYOND SECTION (A) X SECTION LENGTH (FT) X WIRE FACTOR
SECTION |  |  | AMPERES |  |  | AMPERE FEET | AWG | VOLTAGE DROP |  | % DROP | AT POINT
FROM | TO | FEET | AT POINT |  | ACCUM. |  |  | IN SECTION | ACCUM.
|  |  | FIXTURES | TOTAL
CIRCUIT 1-WAP
WAP-4 | WAP-3 | 179 | 1 | 0.5625 | 0.5625 | 100.6875 | 4 | 0.062426 | 0.45442 | 0.18934 | WAP-4
WAP-3 | WAP-2 | 177 | 1 | 0.5625 | 1.125 | 199.125 | 4 | 0.12346 | 0.39199 | 0.16333 | WAP-3
WAP-2 | WAP-1 | 126 | 1 | 0.5625 | 1.6875 | 212.625 | 4 | 0.13183 | 0.26854 | 0.11189 | WAP-2
WAP-1 | PB-3 | 47 | 1 | 0.5625 | 2.25 | 105.75 | 4 | 0.065565 | 0.13671 | 0.056963 | WAP-1
PB-3 | CC | 51 | 0 | 0 | 2.25 | 114.75 | 4 | 0.071145 | 0.071145 | 0.029644 | PB-3
CIRCUIT 2-NAP
NAP-3 | NAP-2 | 178 | 1 | 0.5625 | 0.5625 | 100.125 | 4 | 0.062078 | 0.38397 | 0.15999 | NAP-3
NAP-2 | NAP-1 | 136 | 1 | 0.5625 | 1.125 | 153 | 4 | 0.09486 | 0.3219 | 0.13412 | NAP-2
NAP-1 | PB-4 | 22 | 1 | 0.5625 | 1.6875 | 37.125 | 4 | 0.023017 | 0.22704 | 0.094598 | NAP-1
PB-4 | CC | 195 | 0 | 0 | 1.6875 | 329.0625 | 4 | 0.20402 | 0.20402 | 0.085008 | PB-4
CIRCUIT 3-EAP
EAP-4 | PB-6 | 32 | 1 | 0.5625 | 0.5625 | 18 | 4 | 0.01116 | 0.73796 | 0.30748 | EAP-4
PB-6 | EAP-3 | 142 | 0 | 0 | 0.5625 | 79.875 | 4 | 0.049523 | 0.7268 | 0.30283 | PB-6
EAP-3 | EAP-2 | 165 | 1 | 0.5625 | 1.125 | 185.625 | 4 | 0.11509 | 0.67727 | 0.2822 | EAP-3
EAP-2 | EAP-1 | 88 | 1 | 0.5625 | 1.6875 | 148.5 | 4 | 0.09207 | 0.56219 | 0.23424 | EAP-2
EAP-1 | PB-5 | 16 | 1 | 0.5625 | 2.25 | 36 | 4 | 0.02232 | 0.47012 | 0.19588 | EAP-1
PB-5 | CC | 321 | 0 | 0 | 2.25 | 722.25 | 4 | 0.44779 | 0.44779 | 0.18658 | PB-5
CIRCUIT 4-SAP
SAP-3 | SAP-2 | 168 | 1 | 0.5625 | 0.5625 | 94.5 | 4 | 0.05859 | 0.35817 | 0.14924 | SAP-3
SAP-2 | PB-7 | 74 | 1 | 0.5625 | 1.125 | 83.25 | 4 | 0.051615 | 0.29958 | 0.12482 | SAP-2
SAP-1 | PB-7 | 93 | 1 | 0.5625 | 1.6875 | 156.9375 | 4 | 0.097301 | 0.24796 | 0.10332 | SAP-1
PB-7 | CC | 144 | 0 | 0 | 1.6875 | 243 | 4 | 0.15066 | 0.15066 | 0.062775 | PB-7
|  | Watts |  | Volts | Lamp Loss
LIGHT FIXTURES = |  | 135 |  | 240 | 1 | = | 0.5625 | AMPS/FIXTURE - Conventional
[8 empty] | S. Factor | Min Rating |  | Recommended Fuse
|  | TOTAL AMPS OF CIRCUIT 1(WAP)= |  |  |  |  | 2.25 | 1.25 | 2.8125 |  | 10
|  | TOTAL AMPS OF CIRCUIT 2 (NAP) = |  |  |  |  | 1.6875 | 1.25 | 2.1094 |  | 10
|  | TOTAL AMPS OF CIRCUIT 3 (EAP)= |  |  |  |  | 2.25 | 1.25 | 2.8125 |  | 10
|  | TOTAL AMPS OF CIRCUIT 4 (SAP) = |  |  |  |  | 1.6875 | 1.25 | 2.1094 |  | 10
CONNECTED LOAD = |  | (LINE VOLTAGE X TOTAL CURRENT)/1000
|  | 240 |  |  | x | 7.875 |  |  | 1.89 | KVA
ENCLOSURE RATING= |  | (SUM OF CIRCUIT LOAD/0.8)=
|  | 7.875 |  |  | /0.8 | = | 9.8438 | Amps | 60 | (USE STANDARD 60, 100, OR 200)

## POWER SERVICE DATA
POWER SERVICE DATA
POWER SERVICE | LINE VOLTAGE (VOLTS) | CONNECTED LOAD (kVA) | SERVICE ENTRANCE CABLE (AWG) | ENCLOSURE RATING (AMPS) | CIRCUIT NO. | CIRCUIT LOAD (AMPS) | CIRCUIT FUSE SIZE (AMPS) | CIRCUIT CABLE SIZE (AWG) | MAINTAINING AGENCY
CC | 120/240 | 1.89 | 4 | 60 | WAP | 2.25 | 10 | 4 | ODOT
[5 empty] | NAP | 1.69 | 10 | 4
[5 empty] | EAP | 2.25 | 10 | 4
[5 empty] | SAP | 1.69 | 10 | 4