## Circuit X
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 3 | 12 | 2
Power Service: |  |  | Circuit: | [7 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. | 4 | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
HM-7 | PB-3 | 67 | 0.783 | 0.783 | 52.461 | 4 | 0.032526 | 1.2967 | 0.27014 | HM-7
PB-3 | PB-4 | 68 | 0 | 0.783 | 53.244 | 4 | 0.033011 | 1.2641 | 0.26336 | PB-3
PB-4 | HM-6 | 203 | 0.783 | 1.566 | 317.898 | 4 | 0.1971 | 1.2311 | 0.25648 | PB-4
HM-6 | HM-5 | 255 | 0.783 | 2.349 | 598.995 | 4 | 0.37138 | 1.034 | 0.21542 | HM-6
HM-5 | HM-4 | 310 | 0.783 | 3.132 | 970.92 | 4 | 0.60197 | 0.66265 | 0.13805 | HM-5
HM-4 | PB-2 | 25 | 0.783 | 3.915 | 97.875 | 4 | 0.060683 | 0.060683 | 0.012642 | HM-4
HM-3 | HM-2 | 244 | 0.783 | 0.783 | 191.052 | 4 | 0.11845 | 1.0039 | 0.20915 | HM-3
HM-2 | HM-1 | 243 | 0.783 | 1.566 | 380.538 | 4 | 0.23593 | 0.88548 | 0.18447 | HM-2
HM-1 | PB-5 | 300 | 0.783 | 2.349 | 704.7 | 4 | 0.43691 | 0.64955 | 0.13532 | HM-1
PB-5 | PB-2 | 68 | 0 | 2.349 | 159.732 | 4 | 0.099034 | 0.21263 | 0.044298 | PB-5
PB-2 | CC | 26 | 0.783 | 7.047 | 183.222 | 4 | 0.1136 | 0.1136 | 0.023666 | PB-2
120
240
480