## Circuit X
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | A | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 120 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
SECTION |  |  | AMPERES |  | AMPERE-FEET | AWG | VOLTAGE DROP |  | % DROP | AT POINT
FROM | TO | DESIGN FEET | AT POINT | ACCUM. |  |  | IN SECTION | ACCUM.
AA-3 | PB-3 | 22 | 1.6 | 1.6 | 35.2 | 4 | 0.021824 | 0.35315 | 0.29429 | AA-3
PB-3 | PB-2 | 105 | 0 | 1.6 | 168 | 4 | 0.10416 | 0.33133 | 0.27611
AA-2 | PB-2 | 21 | 1.6 | 1.6 | 33.6 | 4 | 0.020832 | 0.22717 | 0.18931
PB-2 | PB-1 | 94 | 0 | 3.2 | 300.8 | 4 | 0.1865 | 0.20634 | 0.17195
PB-1 | CC-1-PB | 20 | 0 | 4.8 | 96 | 4 | 0.05952 | 0.05952 | 0.0496
AA-1 | CC-1-PB | 68 | 1.6 | 1.6 | 108.8 | 4 | 0.067456 | 0.087296 | 0.072747 | AA-1
CC-1-PB | CC-1 | 5 | 0 | 6.4 | 32 | 4 | 0.01984 | 0.01984 | 0.016533
120
240
480