## PROJECT INFO
PROJECT INFORMATION
PROJECT/PID: | 117955
INTERSECTION NAME: | SR 435 & I-71 NB Ramps
STUDY DATE:
Add Print Headers

## CONDUIT SIZING
CONDUIT | [6 empty] | CABLE AND WIRE | [5 empty] | IS [A] LESS THAN 0.25C? | FINAL CONDUIT NOMINAL DIAMETER
FROM | TO | RUN LENGTH | SIZE/NOMINAL DIAMETER | INSIDE DIAMETER | C | 0.25C | CABLE USE | SPECIFICATION OR MATERIAL | NO. OF CONDUCTORS AWG | NO. CABLES OR WIRES* | a | [A] | [7 empty] | Used to calulate area: |  |  | Specification or Material lookup:
[5 empty] | INSIDE AREA | 25% INSIDE AREA |  |  |  |  | CROSS SECTION AREA | COMBINED CROSS SECTION AREA
|  | FT. | IN. | IN. | SQ. IN. | SQ. IN. |  |  |  |  | SQ. IN. | SQ. IN. |  | IN. | CONDUIT CROSS SECTION AREA |  |  |  |  | CROSS SECTION AREA OF CABLE AND WIRE |  |  | - | IMSA 19-1 OR 20-1 | RHH/RHW/USE | ETHERNET CAT 5E ARMORED | SMARTSENSOR 6 CONDUCTOR | IMSA 50-2 | RG-6/V (COAX) | RG-6/V WITH POWER (COAX) | RG-8/U (COAX) | SMARTSENSOR 8 CONDUCTOR | FIBER, 6 STRAND | FIBER, 12 STRAND | FIBER, 24 STRAND | FIBER, 48 STRAND | FIBER, 72 STRAND | FIBER, 144 STRAND | FIBER, 288 STRAND
CABINET | TB1 | 10 | 4 | 4.026 | 12.72 | 3.18 | SIGNALS | IMSA 19-1 OR 20-1 | 7/C # 14 | 7 | 1.54 | 2.65 | YES | 4 | 0.4 AREA | NOMINAL DIAMETER | INSIDE DIAMETER | INSIDE AREA | 0.25 AREA | SPECIFICATION OR MATERIAL | NO. OF CONDUCTORS AWG | CROSS SECTION AREA, SQ. IN. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[7 empty] | WAVETRONIX RADAR | SMARTSENSOR 8 CONDUCTOR | 8/C # 20 | 5 | 0.85 |  |  |  | - | - | - | - | - | - | - | - |  | 2/C # 14 | 1/C # 14 | 8/C # 24 | 6/C # 20 | 2/C # 14 | 1/C # 18 | 1/C # 18 (COAX) | 1/C # 11 | 8/C # 20 | 6 STRAND | 12 STRAND | 24 STRAND | 48 STRAND | 72 STRAND | 144 STRAND | 288 STRAND
[7 empty] | RADIO ANTENNA | RG-8/U (COAX) | 1/C # 11 | 2 | 0.26 |  |  |  | 0.075 | 0.5 | 0.622 | 0.3 | 0.075 | IMSA 19-1 OR 20-1 | 2/C # 12 | 0.12 |  | 3/C # 14 | 1/C # 12 |  |  |  |  | 2/C # 16 (POWER)
[7 empty] | - | - | - | - | - |  |  |  | 0.1325 | 0.75 | 0.824 | 0.53 | 0.1325 | IMSA 19-1 OR 20-1 | 2/C # 14 | 0.1 |  | 4/C # 14 | 1/C # 10
[7 empty] | - | - | - | - | - |  |  |  | 0.215 | 1 | 1.049 | 0.86 | 0.215 | IMSA 19-1 OR 20-1 | 3/C # 12 | 0.16 |  | 5/C # 14 | 1/C # 8
[7 empty] | - | - | - | - | - |  |  |  | 0.375 | 1.25 | 1.38 | 1.5 | 0.375 | IMSA 19-1 OR 20-1 | 3/C # 14 | 0.13 |  | 7/C # 14 | 1/C # 6
[7 empty] | - | - | - | - | - |  |  |  | 0.51 | 1.5 | 1.61 | 2.04 | 0.51 | IMSA 19-1 OR 20-1 | 4/C # 12 | 0.19 |  | 9/C # 14 | 1/C # 4
[7 empty] | - | - | - | - | - |  |  |  | 0.84 | 2 | 2.067 | 3.36 | 0.84 | IMSA 19-1 OR 20-1 | 4/C # 14 | 0.16 |  | 12/C # 14 | 1/C # 2
[7 empty] | - | - | - | - | - |  |  |  | 1.1975 | 2.5 | 2.469 | 4.79 | 1.1975 | IMSA 19-1 OR 20-1 | 5/C # 12 | 0.23 |  | 15/C # 14 | 1/C # 1
[7 empty] | - | - | - | - | - |  |  |  | 1.845 | 3 | 3.068 | 7.38 | 1.845 | IMSA 19-1 OR 20-1 | 5/C # 14 | 0.19 |  | 18/C # 14 | 1/C # 1/0
[7 empty] | - | - | - | - | - |  |  |  | 2.475 | 3.5 | 3.548 | 9.9 | 2.475 | IMSA 19-1 OR 20-1 | 7/C # 12 | 0.3 |  | 25/C # 14 | 1/C # 2/0
[7 empty] | - | - | - | - | - |  |  |  | 3.18 | 4 | 4.026 | 12.72 | 3.18 | IMSA 19-1 OR 20-1 | 7/C # 14 | 0.22 |  | 2/C # 12 | 1/C # 3/0
[7 empty] | - | - | - | - | - | [8 empty] | IMSA 19-1 OR 20-1 | 9/C # 12 | 0.4 |  | 3/C # 12 | 1/C # 4/0
[7 empty] | - | - | - | - | - |  |  |  |  | NOMINAL DIAMETER | 0.25 AREA |  |  | IMSA 19-1 OR 20-1 | 9/C # 14 | 0.33 |  | 4/C # 12
[7 empty] | - | - | - | - | - |  |  |  |  | 4 | 3.18 |  |  | IMSA 19-1 OR 20-1 | 12/C # 12 | 0.5 |  | 5/C # 12
TB1 | SP-2 | 10 | 4 | 4.026 | 12.72 | 3.18 | SIGNALS | IMSA 19-1 OR 20-1 | 7/C # 14 | 7 | 1.54 | 2.65 | YES | 4 |  | 3.5 | 2.48 |  |  | IMSA 19-1 OR 20-1 | 12/C # 14 | 0.41 |  | 7/C # 12
[7 empty] | WAVETRONIX RADAR | SMARTSENSOR 8 CONDUCTOR | 8/C # 20 | 5 | 0.85 |  |  |  |  | 3 | 1.85 |  |  | IMSA 19-1 OR 20-1 | 15/C #12 | 0.58 |  | 9/C # 12
[7 empty] | RADIO ANTENNA | RG-8/U (COAX) | 1/C # 11 | 2 | 0.26 |  |  |  |  | 2.5 | 1.2 |  |  | IMSA 19-1 OR 20-1 | 15/C # 14 | 0.48 |  | 12/C # 12
[7 empty] | - | - | - | - | - |  |  |  |  | 2 | 0.84 |  |  | IMSA 19-1 OR 20-1 | 18/C # 12 | 0.74 |  | 15/C #12
[7 empty] | - | - | - | - | - |  |  |  |  | 1.5 | 0.51 |  |  | IMSA 19-1 OR 20-1 | 18/C # 14 | 0.55 |  | 18/C # 12
[7 empty] | - | - | - | - | - |  |  |  |  | 1.25 | 0.38 |  |  | IMSA 19-1 OR 20-1 | 25/C # 12 | 1 |  | 25/C # 12
[7 empty] | - | - | - | - | - |  |  |  |  | 1 | 0.22 |  |  | IMSA 19-1 OR 20-1 | 25/C # 14 | 0.82
[7 empty] | - | - | - | - | - |  |  |  |  | 0.75 | 0.13 |  |  | RHH/RHW/USE | 1/C # 2 | 0.229 | Cable Use:
[7 empty] | - | - | - | - | - |  |  |  |  | 0.5 | 0.08 |  |  | RHH/RHW/USE | 1/C # 4 | 0.173 | - | SIGNALS | POWER/LIGHTING | COMMUNICATIONS | WAVETRONIX RADAR | LOOP LEAD-IN | VIDEO | RADIO ANTENNA
[7 empty] | - | - | - | - | - | [8 empty] | RHH/RHW/USE | 1/C # 6 | 0.138 | - | - | - | - | - | - | - | -
[7 empty] | - | - | - | - | - | [8 empty] | RHH/RHW/USE | 1/C # 8 | 0.107 |  | IMSA 19-1 OR 20-1 | RHH/RHW/USE | ETHERNET CAT 5E ARMORED | SMARTSENSOR 6 CONDUCTOR | IMSA 50-2 | RG-6/V (COAX) | RG-8/U (COAX)
[7 empty] | - | - | - | - | - | [8 empty] | RHH/RHW/USE | 1/C # 10 | 0.075 |  |  |  | FIBER, 6 STRAND | SMARTSENSOR 8 CONDUCTOR |  | RG-6/V WITH POWER (COAX)
[7 empty] | - | - | - | - | - | [8 empty] | RHH/RHW/USE | 1/C # 12 | 0.061 |  |  |  | FIBER, 12 STRAND
[7 empty] | - | - | - | - | - | [8 empty] | RHH/RHW/USE | 1/C # 14 | 0.053 |  |  |  | FIBER, 24 STRAND
[7 empty] | - | - | - | - | - | [8 empty] | ETHERNET CAT 5E ARMORED | 8/C # 24 | 0.13 |  |  |  | FIBER, 48 STRAND
UPS | SP-2 | 15 | 2 | 2.067 | 3.36 | 0.84 | POWER/LIGHTING | RHH/RHW/USE | 1/C # 6 | 3 | 0.414 | 0.414 | YES | 2 | [5 empty] | SMARTSENSOR 6 CONDUCTOR | 6/C # 20 | 0.17 |  |  |  | FIBER, 72 STRAND
[7 empty] | - | - | - | - | - | [8 empty] | IMSA 50-2 | 2/C # 14 | 0.1 |  |  |  | FIBER, 144 STRAND
[7 empty] | - | - | - | - | - | [8 empty] | RG-6/V (COAX) | 1/C # 18 | 0.06 |  |  |  | FIBER, 288 STRAND
[7 empty] | - | - | - | - | - | [8 empty] | RG-6/V WITH POWER (COAX) | 1/C # 18 (COAX) | 0.16
[7 empty] | - | - | - | - | - | [8 empty] | RG-6/V WITH POWER (COAX) | 2/C # 16 (POWER) | 0.16
[7 empty] | - | - | - | - | - | [8 empty] | RG-8/U (COAX) | 1/C # 11 | 0.13
[7 empty] | - | - | - | - | - | [8 empty] | SMARTSENSOR 8 CONDUCTOR | 8/C # 20 | 0.17
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 6 STRAND | 6 STRAND | 0.2
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 12 STRAND | 12 STRAND | 0.2
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 24 STRAND | 24 STRAND | 0.2
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 48 STRAND | 48 STRAND | 0.2
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 72 STRAND | 72 STRAND | 0.2
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 144 STRAND | 144 STRAND | 0.42
[7 empty] | - | - | - | - | - | [8 empty] | FIBER, 288 STRAND | 288 STRAND | 0.56
[7 empty] | - | - | - | - | - | [8 empty] | RHH/RHW/USE | 1/C # 1 | 0.245 | Got new power cable info from: |  | http://www.standard-wire.com/downloads/SWC_Catalog.pdf
[20 empty] | RHH/RHW/USE | 1/C # 1/0 | 0.3025 | REMEMBER TO CONVERT ALL TO SQ. IN!!!!!!!!!!!!!!!!!!!
* NOTE: INCLUDE GROUNDING CONDUCTOR IN WIRE COUNT FOR LIGHTING CIRCUITS OF NOTATION "WITH GROUND." | [19 empty] | RHH/RHW/USE | 1/C # 2/0 | 0.3721
[20 empty] | RHH/RHW/USE | 1/C # 3/0 | 0.4356
(Use additional spreadsheets for additional conduit runs) | [19 empty] | RHH/RHW/USE | 1/C # 4/0 | 0.5329