## US23 AT RATHMELL
VOLTAGE DROP CALCULATIONS | [10 empty] | BASIC FORMULAS AND DATA: |  |  |  | VOLTAGE DROP STUDY
County-Route-Section: |  | US23 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 3
Power Service: |  | LC | Leg: | A | [6 empty] | LED ELECTRICAL DATA |  |  |  | WIRE SIZE
Supply Voltage: |  | 480 | [8 empty] | LAMP | LINE VOLTS | LINE AMP. |  | 14 | 3.1
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | WATTAGE |  | OPERATING |  | 12 | 2
|  | No. | 4 | AWG. | 0.31 | [5 empty] | 187 | 480 | 0.38958 |  | 10 | 1.2
[15 empty] | 8 | 0.78
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 | [6 empty] | 6 | 0.49
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 | [6 empty] | 4 | 0.31
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 | [6 empty] | 2 | 0.19
|  | Wire Factor Used (Three - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Leg: 'A' |  |  |  |  | 1/0 | 0.12
[15 empty] | 2/0 | 0.1
Section |  |  | Amperes |  | Ampere-Feet | AWG | Voltage Drop |  | % Drop | At Point |  |  |  |  | 4/0 | 0.079
From | To | FEET | At Point | Accum. |  |  | In Section | Accum.
A-2 | PB | 51 | 0.38958 | 0.38958 | 19.8687 | 4 | 0 | 0 | 0 | A-2 | LIGHTING POWER SERVICE DATA
[11 empty] | CONTROL CENTER | LINE VOLTAGE (VOLTS) | CONNECTED LOAD (KVA) | SERVICE ENTRANCE CABLE (AWG) | ENCLOSURE RATING (AMPS) | LEG | CIRCUIT LOAD (AMPS) | CIRCUIT FUSE SIZE (AMPS) | CIRCUIT CABLE SIZE (AWG) | MAINTAINING AGENCY
A-3 | PB | 25 | 0.38958 | 0.38958 | 9.7396 | 4 | 0 | 0 | 0 | A-3
PB | PB | 157 | 0 | 0.77917 | 122.3292 | 4 | 0 | 0 | 0 | PB
A-1 | PB | 46 | 0.38958 | 0.38958 | 17.9208 | 4 | 0 | 0 | 0 | A-1 | 3-WIRE, 480V PAD MOUNT CONTROLLER | 480 | 0.935 | #6 | 100 | A | 1.5583 | 15 A | 4 | CITY OF COLUMBUS
PB | PB | 162 | 0 | 1.1687 | 189.3375 | 4 | 0 | 0 | 0 | PB | [5 empty] | B | 0.38958 | 15 A | 4
[16 empty] | C | 0.38958 | 15 A | 4
A-4 | PB | 84 | 0.38958 | 0.38958 | 32.725 | 4 | 0 | 0 | 0 | A-4
PB | LC | 25 | 0 | 1.5583 | 38.9583 | 4 | 0.036231 | 0.036231 | 0.0075482 | PB
1. AT A POINT WHERE A CIRCUIT BRANCHES (I.E., PB) THE ACCUMULATED LOAD BEYOND
THIS POINT IS SHOWN IN THE "AT POINT" COLUMN TO FACILITATE CHECKING.
VOLTAGE DROP CALCULATIONS
County-Route-Section: |  | US23 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 3
Power Service: |  | LC | Leg: | B
Supply Voltage: |  | 480
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31
|  | No. | 4 | AWG. | 0.31
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000
|  | Wire Factor Used (Three - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Leg: 'B'
Section |  |  | Amperes |  | Ampere-Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | FEET | At Point | Accum. |  |  | In Section | Accum.
B-1 | PB | 20 | 0.38958 | 0.38958 | 7.7917 | 4 | 0.0072463 | 0.010869 | 0.0022645 | B-1
PB | LC | 10 | 0 | 0.38958 | 3.8958 | 4 | 0.0036231 | 0.0036231 | 0.00075482 | PB
1. AT A POINT WHERE A CIRCUIT BRANCHES (I.E., PB) THE ACCUMULATED LOAD BEYOND
THIS POINT IS SHOWN IN THE "AT POINT" COLUMN TO FACILITATE CHECKING.
VOLTAGE DROP CALCULATIONS
County-Route-Section: |  | US23 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 3
Power Service: |  | LC | Leg: | C
Supply Voltage: |  | 480
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31
|  | No. | 4 | AWG. | 0.31
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000
|  | Wire Factor Used (Three - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Leg: 'A'
Section |  |  | Amperes |  | Ampere-Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | FEET | At Point | Accum. |  |  | In Section | Accum.
C-1 | PB | 80 | 0.38958 | 0.38958 | 31.1667 | 4 | 0.028985 | 0.032608 | 0.0067934 | C-1
PB | LC | 10 | 0 | 0.38958 | 3.8958 | 4 | 0.0036231 | 0.0036231 | 0.00075482 | PB
1. AT A POINT WHERE A CIRCUIT BRANCHES (I.E., PB) THE ACCUMULATED LOAD BEYOND
THIS POINT IS SHOWN IN THE "AT POINT" COLUMN TO FACILITATE CHECKING.

## OLD
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | 45 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 45 | Circuit: | [7 empty] | 10 | 1.2
Supply Voltage: |  | 45 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. |  | AWG. | [6 empty] | 6 | 0.49
|  | No. | 8 | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'X' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
a | b | 100 | 5 | 500 | 50000 | 4 | 31 |  | 0 | a
120
240
480

## US23 AT RATHMELL (2)
VOLTAGE DROP CALCULATIONS | [10 empty] | BASIC FORMULAS AND DATA: |  |  |  | VOLTAGE DROP STUDY
County-Route-Section: |  | US23 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2
Power Service: |  | CC-'A' | Circuit: | CKT 1 | [6 empty] | LED ELECTRICAL DATA |  |  |  | WIRE SIZE
Supply Voltage: |  | 480 | [8 empty] | LAMP | LINE VOLTS | LINE AMP. |  | 14 | 3.1
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | WATTAGE |  | OPERATING |  | 12 | 2
|  | No. | 4 | AWG. | 0.31 | [5 empty] | 100 | 480 | 0.31 |  | 10 | 1.2
[11 empty] | 150 | 480 | 0.45 |  | 8 | 0.78
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  |  | 200 | 480 | 0.53 |  | 6 | 0.49
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 250 | 480 | 0.7 |  | 4 | 0.31
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 310 | 480 | 0.8 |  | 2 | 0.19
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Circuit: '1' | 400 | 480 | 1 |  | 1/0 | 0.12
[11 empty] | 1000 | 480 | 2.5 |  | 2/0 | 0.1
Section |  |  | Amperes |  | Ampere-Feet | AWG | Voltage Drop |  | % Drop | At Point |  |  |  |  | 4/0 | 0.079
From | To | FEET | At Point | Accum. |  |  | In Section | Accum.
A-1-3 | A-1-4 | 175 | 0.7 | 0.7 | 122.5 | 4 | 0.07595 | 0.27559 | 0.057415 | A-1-3 | LIGHTING POWER SERVICE DATA
A-1-4 | PB | 180 | 0.7 | 1.4 | 252 | 4 | 0.15624 | 0.19964 | 0.041592 | A-1-4 | POWER SERVICE | LINE VOLTAGE (VOLTS) | CONNECTED LOAD (KVA) | SERVICE ENTRANCE CABLE (AWG) | ENCLOSURE RATING (AMPS) | CIRCUIT NO. | CIRCUIT LOAD (AMPS) | CIRCUIT FUSE SIZE (AMPS) | CIRCUIT CABLE SIZE (AWG) | MAINTAINING AGENCY
A-1-2 | PB | 155 | 0.7 | 0.7 | 108.5 | 4 | 0.06727 | 0.11067 | 0.023056 | A-1-2
A-1-1 | PB | 60 | 0.7 | 0.7 | 42 | 4 | 0.02604 | 0.06944 | 0.014467 | A-1-1 | CC-'A' | 480 | 1.344 | #1 | 150 | CKT 1 | 2.8 | 20 | 4 | CITY OF COLUMBUS
PB | CC-'A' | 25 | 0 | 2.8 | 70 | 4 | 0.0434 | 0.0434 | 0.0090417 | PB
1. AT A POINT WHERE A CIRCUIT BRANCHES (I.E., PB) THE ACCUMULATED LOAD BEYOND
THIS POINT IS SHOWN IN THE "AT POINT" COLUMN TO FACILITATE CHECKING.