## CRF
DOCUMENT NAME: |  |  | WSP FWW Scope of Services_ODOT
No | Document/ Drawing Number | Page | Comment | Comment By | Response | Response By | Comment | Comment By | Open-Closed (By Reviewer)
1 | WSP FWW Scope of Services_ODOT.pdf | PDF 1/5 | Can ODOT get an updated copy of the cost estimates? | ODOT | Once it is redesigned to meet ODOT requirements. | WSP | This response is fine. | Spinosa | Closed
2 | WSP FWW Scope of Services_ODOT.pdf | PDF 1/5 | Adding foundations will not be practical for this project. Design of the cap should utilize the existing pile capacity. The existing foundations and walls supporting the Caps were not designed to LRFD standards. It will be difficult, costly and impractical to update some elements to LRFD guidelines. Consider treating the superstructure as new (LRFD) only. | ODOT | Will consider. | WSP | See notes provided from ODOT District 8 and OSE meeting. | Shell | Closed
3 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | It should be noted that other alternative may be required as the project moves out of planning/feasibility phase of work. ODOT should be consulted on structure type study. Note: Prestressed composite box beams would be an allowable struture type. However, hanging anything from the boxbeams is prohibited based on ODOT Standards. | ODOT | We should discuss. Is this true even if inserts are cast in webs as opposed to drilled in? Inherent in the design is the use of polypropylene fiber to prevent spalling under the heat of a typical design fire (WSP used it on a similar tunnel for C70 in Denver). That should also help inserts if cast in. | WSP | Based on meeting held on 12/5/23, the decision on appropriate structure type will be discussed with WSP once ODOT reviews beam information submitted.. | Spinosa | Closed
4 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Composite | ODOT | Will comply. | WSP | This response is fine. | Shell | Closed
5 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Or shallow beam system | ODOT | Will comply. | WSP | This response is fine. | Shell | Closed
6 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | The existing foundations and walls supporting the Caps were not designed to LRFD standards. It will be difficult, costly and impractical to update some elements to LRFD guidelines. Consider treating the superstructures as new (LRFD) only. | ODOT | Will consider. | WSP | See notes provided from ODOT District 8 and OSE meeting. | Shell | Closed
7 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Fans, signs, lights etc. cannot be hung from boxbeams. | ODOT | Please see 3, above. | WSP | See notes provided from ODOT District 8 and OSE meeting. | Shell | Closed
8 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Please provide as-builts of what extra piling was installed and pile log information you have in your archive storage. | ODOT | We have locations on file, with many uniquely numbered on as-builts, but need to look into driving logs. | WSP | Will need this information when WSP's final report is submitted. | Spinosa | Open
9 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Composite slabs on boxbeams shall be designed as continuous | ODOT | Will comply for superimposed dead load and live load. | WSP | This response is fine. | Shell | Closed
10 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Concerns with having fans over live traffic | ODOT | Understood, however, this is now common practice in US road tunnels and methods have been developed for safely supporting these large dynamic loads in a positive manner, transferring reaction to a position above the boxes. | WSP | See conceptual comments from the notes provided from ODOT District 8 and OSE meeting. | Shell | Open
11 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Air flow modelling will be needed to confirm this configuration will work for the design fire load | ODOT | Agreed. The current ventilation concept is based on a preliminary one-dimensional analysis that assumed a 100MW fire load suppressed 60% by a fixed fire supression system. These assumed criteria will need to be confirmed and accepted by ODOT and the AHJ. A more refined and detailed analysis will be performed in a later phase once the design fire criteria is established. | WSP | This response is fine. | Shell | Closed
12 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Should "ceiling" structural units also have fireproofing? | ODOT | See 13, below. | WSP | Further analysis on this topic is needed in order to "close" it. Prior to any final design commencing, this issue will need to be resolved and included in final scope. Including tiling would not be ODOT's preference unless required for lighting rquirements and/or fireproofing. Issue will need to be resolved prior to final scope. | Spinosa | Open
13 | WSP FWW Scope of Services_ODOT.pdf | PDF 2/5 | Is fire proofing needed on ceiling? Is tiling needed? | ODOT | Structural fire proofing is assumed to be required at the ceiling. Design analysis will need to be performed to confirm. While other alternatives exist, we are considering polypropylene fiber additives to the concrete mix for the girders to prevent spalling under design fire load. This is similar to structural design approach used on C70 in Denver. Tiling is not required but may be an ODOT maintenance preference. Tiling has not been included in preliminary estimates. | WSP | See notes provided from ODOT District 8 and OSE meeting. | Shell | Closed
14 | WSP FWW Scope of Services_ODOT.pdf | PDF 3/5 | Use AASHTO LRFD for pedestrian per BDM 303.2. (probably 90 psf) | ODOT | OK, but need to coordinate with the park designers. This may limit soil depth and what is planted in the park. | WSP | See notes provided from ODOT District 8 and OSE meeting. | Shell | Closed
15 | WSP FWW Scope of Services_ODOT.pdf | PDF 3/5 | ODOT Standards | ODOT | Will comply. | WSP | This response is fine. | Shell | Closed
16 | WSP FWW Scope of Services_ODOT.pdf | PDF 3/5 | Utilities in boxbeams is prohibited. Follow BDM 310.4. | ODOT | Will comply. | WSP | See notes provided from ODOT District 8 and OSE meeting. | Shell | Closed
17 | WSP FWW Scope of Services_ODOT.pdf | PDF 3/5 | Inflationary costs per ODOT's inflaction calculator should also be included. | ODOT | Will comply. | WSP |  | Spinosa | Closed
18 | WSP FWW Scope of Services_ODOT.pdf | PDF 3/5 | Existing borings are sufficient for design efforts at current level. | ODOT | Agreed. | WSP |  | Spinosa | Closed
19 | WSP FWW Scope of Services_ODOT.pdf | PDF 3/5 | FHWA will need to be included. The contact at the Ohio Division will be provided by ODOT | ODOT | Agreed. | WSP |  | Spinosa | Closed
20 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | SCADA system and housing controls needs to be examined. | ODOT | Understood. | WSP | This topic needs to remain open for coordination prior to final scoping once local sponosring agency is ready to move forward. | Spinosa | Open
21 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | Controls for these system need to be enclosed and secure with access and substantial parking for emergency and maintenance vehicles. | ODOT | Agreed. | WSP | This topic needs to remain open for coordination prior to final scoping once local sponosring agency is ready to move forward. | Spinosa | Open
22 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | The TMC will monitor traffice operations; however, the SCADA system will need to include monitoring capabilities. There will need to be a tunnel operations and maintenance manual developed that will make final determinations on monitoring. It is not correct at this time that ODOT TMC will be monitoring the tunnel systems. | ODOT | This concept of operations decision is critical to the criteria development for the control, monitoring and activation of tunnel systems - particularly for incident/emergency response. Provision of automatic, manual and manual override cpabilities of the fire life safety and traffic control systems will be dependent on this operational decision. This will be an ongoing discussion between the City of Cincinnati, Hamilton County, and ODOT. | WSP | This topic needs to remain open for coordination prior to final scoping once local sponosring agency is ready to move forward. | Spinosa | Open
23 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | Suggest one of the requirements of this task is an ODOT/City/County/WSP meeting to discuss signing prior to finalizing the concept ODOT and KYTC will need to review the signing plan. | ODOT | Understood. | WSP | Based on 12/5/23 meeting, continued coordination will occur with technical leads. | Spinosa | Closed
24 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | Details need to be worked out early in the preliminary design to ensure this is feasible. | ODOT | Agreed. | WSP | Based on 12/5/23 meeting, continued coordination will occur with technical leads. | Spinosa | Closed
25 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | ODOT would like to have the opportunity to review once developed. | ODOT | Understood. | WSP | No commnents on the Scope of Work. ODOT's expectation is the final work products, i.e. Conceptaual Layout Plans, renderings/graphics, cross sections, etc. completed by KZF will be submitted along with the final work product being prepared by WSP. | Spinosa | Closed
26 | WSP FWW Scope of Services_ODOT.pdf | PDF 4/5 | Signage concepts should also identify other advanced warning signs (Hazardous Cargo notifications) in the region that will need update/added. Routes that may need to be included are I-71, I-75, I-471, and US 50 | ODOT | Understood. | WSP | Based on 12/5/23 meeting, continued coordination will occur with technical leads. | Spinosa | Closed