## Electrical
Procedure Description |  | Frequency | [8 empty] | Recommended (Rec.) or Required (Req.) | Tunnel Closure Required? | Responsible Party |  |  | Scope/Requirements | Fall 2021 Inpsection
|  | Weekly | Monthly | Bi-Monthly | Quarterly | Semi-Annually | Annually | Tri-Annually | Biennially | Quinquennial |  |  | ODOT | Consultant | 3rd Party (Mechanic, Electrician, etc.) |  | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance
1.1 Tunnel Closed Notification/Closed Circuit TV | [15 empty] | Manufacturers O&M Manual for CCTV - Not Provided.
1 | Clean, align, and focus all cameras after tunnel washing |  |  |  |  | X |  |  |  |  | Rec. | Y | O |  |  | Recommended maintenance intervals by FHWA.
2 | Test tunnel closed notification system | [5 empty] | X |  |  |  | Rec. | Y |  |  | Elec | Recommended maintenance intervals by ODOT.
1.2 Emergency Lighting - Buildings
1 | Operate test buttons on emergency light fixtures |  | X |  |  | X |  |  |  |  | Req. | N | O |  | Elec | Per NFPA 101, section 7.9.3 : 1) functional testing to be conducted every 3 to 5 weeks (beyond 30 days to be approved by AHJ) OR 2) self-testing/self diagnosticbattery-operated automatic test once every 30 days for 30 seconds. A visual inspection at invervals not exceeding 30 days OR 3) Computer-based, self-testing/self-diagnostic battery-operated, automatic test not less than every 30 days for a minumum of 30 seconds.
2 | Operate battery pack for emergency lighting for 90 minutes | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 101, section 7.9.3 : 1) if the emergency lighting system is self-testing/self-diagnostic, then the equipment shall be fully operation for the duration of the 90 minutes test OR 2) if the system if computer-based, then the 90 minutes test shall be performed automatically.
1.3 Electrical Switchboard and Switchgear | [15 empty] | Recommended maintenance intervals by FHWA:
1 | Inspect switchgear bus and connections by infrared scanning | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommendations: On the circuit breaker molded case there should not be: 1) no traces of grime (grease), excessive dust or condensation which all reduce insulation. 2) no signs of burns or cracks which could weaken the case and thus its capacity to withstand short-circuits. Preventative maintenance recommendation for molded case: 1) A visual inspection of its condition and cleaning with a dry cloth or a Q14vacuum cleaner. All cleaning products with solvents Q14are strictly forbidden. 2) Measuring the insulation every five years and following trips due to a short-circuit. Replace the circuit breaker if there are signs of burns or cracks. The arc chutes must be regularly checked. The fins of the arc chutes may be blackened (due to the gases produced at In) but must not be significantly damaged. What is more, the filters must not be blocked to avoid internal overpressures. Use a vacuum cleaner rather than a cloth to remove dust from the outside of the arc chutes. Regular operation is required to maintain the normal performance level of each part involved in the opening and closing cycles. In installations where power circuit breakers are used in source changeover systems, it is advised to periodically operate the circuit breaker for the alternate source. Preventative maintenance for MX and XF shunt releases and MN undervoltage release consists of periodically cheaking operation at minimum values. Auxiliary wiring must be regularly checked and replaced as needed, particularly if there are vibrations, high ambient temperatures or corrosive atmospheres. Periodic checks on the spring charging motor operation and the charging time are required to ensure the device function. To ensure correct operation of electronic trip unit, it is necessary to periodically check: • the chain of action resulting in a trip • the response time as a function of the level of the fault current. Periodic checks on the orders (read, write, commands) transmitted by the communication bus are required to maintain a high degree of reliability and confidence in the communication system. If fixed circuit breaker connections are not made with Schneider Electric recommendations (tightening torque, hardware, and contact washer), then regularly check the temperature-rise points. If there is a change in color of copper or tinning: • dismantle the connections • clean and scrape the contact surfaces • then reassemble the connections using new hardware. Check the terminals. Drawout circuit breakers connections require periodic cleaning. Always inspect the switchboard after a fault. General switchboard inpsection and cleaning: 1. Vacuum the switchboard interior to remove any dirt or dust deposits. Wipe all bus bars, insulators, cables, etc., with a clean, dry, lint-free cloth. 2. Check the switchboard interior carefully for moisture, condensation build-up, or signs of any previous wetness. Inspect all conduit entrances and cracks between the enclosure panels for dripping leaks. Take the necessary steps to eliminate the moisture and seal off all leaks. 3. Inspect the switchboard for any signs of overheating. Discoloration and flaking of insulation or metal parts are indications of overheating. 4. Check for signs of rodent nesting in the switchboard. 5. Carefully inspect all devices for any visibly worn-out, cracked, or missing parts. 6. Manually open and close switches and circuit breakers several times to verify they are working properly. 7. Verify that all key interlocks and door interlocking provisions are working properly. Bus Bar Joints, Lug Terminations, and Insulating Materials 1. Bus bar joints are maintenance-free. Do not retighten them after the pre-energizing checkout procedure is complete. 2. Check all bus bar joints and terminal lugs for any pitting, corrosion, or discoloration resulting from high temperatures or subjection to high fault conditions. If any damage has occurred, replace the bus bars or lugs. If cleaning is required, use Lectra-Clean®, made by CRC. 3. Inspect all insulating materials. Before re-energizing the switchboard, replace insulators with any visible damage (such as cracks). Bolt-Loc switch maintenance: 1. Exercise the operating mechanism at least once a year to ensure proper operation. 2. The Bolt-Loc switch is shipped from the factory properly lubricated. Periodic cleaning and lubrication of the switch is required. The maintenance interval between lubrications depends on factors such as usage and ambient conditions. The maximum recommended maintenance interval is one year for current-carrying parts and five years for operating mechanisms. Exercise circuit breakers at least once a year to ensure proper operation. For general maintenance: 1. Trip the circuit breaker by pushing the Push-To-Trip or “Open” button located on the face of the circuit breaker. Refer to the appropriate circuit breaker manual for the specific location of this button. 2. Manually open and close the circuit breaker two to three times. QMB/QMJ/QMQB1 Fusible Switches 1. Periodically exercise the switch to ensure proper operation. This period should not exceed one year. 2. Check the cover interlock with the switch in the ON position. The cover should not open using normal hand force. 3. Inspect the switch interior for any damaged or cracked parts, and replace as necessary. 4. For fusible switch units, check the fuse mounting clips or bolted contact area for corrosion or discoloration (indicating overheating). Replace them if necessary. 5. For additional maintenance instructions, see the label on the inside of the door. After the equipment in switchgear has been lubricated, perform the following steps. 1) Inspect all components for cracks, loose parts, and weather or chemical damage. 2) If cracks or strain damage are suspected, remove the unit from service. If cracked components are detected, replace them before returning unit to use. 3) Periodically check for distortion of the traveling lifter. If distortion is found: — Verify that the rails and sections are aligned. — Verify that the carriage and winch mechanism have been installed correctly. — Verify that the cable has been fastened securely to the winch drum. — Verify that the gears are well lubricated. NOTE: For normal operation, use a heavy gear lubricant. In very dirty or gritty conditions, it is advisable to use a dry lubricant such as dry graphite to lubricate the gears. Never allow the gears to run dry. 4) If applicable, remove handling means and any obstructions from the top of the unit that could inhibit operation of the traveling lifter. 5) Thoroughly inspect the traveling lifter wire cable. Pay close attention to cable sections, such as parts passing over sheaves or wound on the drum, which are normally hidden during inspection or maintenance procedures.Contact Schneider Electric Services at 1-888-778-2733 if the cable shows any of the following signs of deterioration: — Kinking, crushing, cutting, or unstranding — Corroded, cracked, bent, or broken wires — Worn end connections 6) Always keep the exterior finish in good condition to protect against corrosive damage. When damage is noticed, remove the finish to bare metal and refinish using a high-quality primer and finish coat. 7) Be certain that all the warning labels are still in place and readable. If the warning labels become unreadable or are destroyed, contact your local Schneider Electric sales office. 8) Do not repair any parts that are worn, cracked, deformed, misaligned, or severely corroded. Repairing parts does not ensure satisfactory or safe performance. Do not substitute other manufacturers’ parts. 9) Record all inspections and maintenance performed on the traveling lifter in a maintenance log. Inspect the SPD periodically to maintain reliable system performance and continued transient voltage surge suppression. Periodically check the state of the diagnostic display panel LED status indicators. Routinely use the built-in diagnostics to inspect for inoperative modules.
2 | Perform ultrasonic inspection of medium voltage switchgear bus supports, insulators, and barriers | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec
3 | Visually inspect all equipment for unusual conditions | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec
4 | Check tightness of all connections | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec
5 | Review results of last visual, infrared, and ultrasonic inspection | [6 empty] | X |  |  | Rec. | N |  | C |  |  | 2021-09-11 | Infrared inspection was performed on each piece of electrical equipment and no deficiencies were found. | None.
6 | After power shutdown, clean entire switchgear interior | [6 empty] | X |  |  | Rec. | N |  |  | Elec
7 | Clean all bus insulators and check for cracks and chips | [6 empty] | X |  |  | Rec. | N |  |  | Elec
8 | Clean, lubricate (if applicable), and verify operation of all control switches, auxiliary relays, and devices | [6 empty] | X |  |  | Rec. | N |  |  | Elec
9 | Clean, lubricate, adjust, and add anti-oxidant grease to contacts of all disconnect switches | [6 empty] | X |  |  | Rec. | N |  |  | Elec
10 | Clean and perform insulation resistance testing on all lighting arrestors | [6 empty] | X |  |  | Rec. | N |  |  | Elec
11 | Perform insulation resistance testing on any bus bars | [6 empty] | X |  |  | Rec. | N |  |  | Elec
12 | Perform calibration test and verify proper operation of all meters | [6 empty] | X |  |  | Rec. | N |  |  | Elec
Low Voltage Air Circuit Breakers
13 | Remove covers and thoroughly clean each breaker and contact surfaces | [6 empty] | X |  |  | Rec. | N |  |  | Elec
14 | Apply anti-oxidant grease to breaker's main contacts | [6 empty] | X |  |  | Rec. | N |  |  | Elec
15 | Lubricate and verify opeation of all mechanisms | [6 empty] | X |  |  | Rec. | N |  |  | Elec
16 | Apply current equal to 90 to 110 percent of the breaker trip coil setting to verify proper pick-up of tripping mechanism | [6 empty] | X |  |  | Rec. | N |  |  | Elec
17 | Record trip times for long-time, short-time instaneous, and ground fault breakers when passing loads equal to multiples of their listed ratings through each phase of the breaker | [6 empty] | X |  |  | Rec. | N |  |  | Elec
18 | Measure contact resistance and adjust where possible | [6 empty] | X |  |  | Rec. | N |  |  | Elec
19 | Perform and record results of insulation resistance test from each pole to other two poles and to ground | [6 empty] | X |  |  | Rec. | N |  |  | Elec
20 | Clean and lubricate breaker carriage and racking mechanism on any draw out breakers | [6 empty] | X |  |  | Rec. | N |  |  | Elec
Modled Case Circuit Breakers
21 | Inspect breaker for proper installation | [6 empty] | X |  |  | Rec. | N |  |  | Elec
22 | Remove cover (if possible) and fully clean interior and exterior | [6 empty] | X |  |  | Rec. | N |  |  | Elec
23 | Inspect for burning, overheating, wear, and proper alighment | [6 empty] | X |  |  | Rec. | N |  |  | Elec
24 | Perform contact resistance and insulation resistance measurements and test | [6 empty] | X |  |  | Rec. | N |  |  | Elec
25 | Apply current equal to 300 percent of breaker rating to test the long-time element | [6 empty] | X |  |  | Rec. | N |  |  | Elec
26 | Test and compare any breakers with instantaneous trip units to manufacturer's characteristic curve | [6 empty] | X |  |  | Rec. | N |  |  | Elec
Automatic Transfer Switch (600 Volt Class)
27 | After total outage is obtained, clean all contact surfaces, apply anti-oxidant contact grease, measure and record contact resistance, and make any adjustments if necessary | [6 empty] | X |  |  | Rec. | N |  |  | Elec
28 | Lubricate bearings, links, pins, and cams | [6 empty] | X |  |  | Rec. | N |  |  | Elec
29 | Perform insulation resistance test | [6 empty] | X |  |  | Rec. | N |  |  | Elec
30 | Test all settings of voltage, frequency sensing, and timing relays | [6 empty] | X |  |  | Rec. | N |  |  | Elec
Low Voltage Insulated Cable (Less Than 600 Volts)
31 | Check all cable terminations for tightness | [6 empty] | X |  |  | Rec. | N |  |  | Elec
32 | Perform and record results of insulation resistance test from each phase to the other two and to ground for one minute using a test voltage of 1,000 volts Direct Current (DC). Compare results with previous test. | [6 empty] | X |  |  | Rec. | N |  |  | Elec
1.4 Masterpact NT and NW Circuit Breakers
Case
1 | Measure insulation resistance | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Device
2 | Check the general condition of the device (accessory cover, trip unit, case, cradle, connections) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Mechanism
3 | Open/close device manually and electrically | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
4 | Charge device electrically | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
5 | Check complete closing of device’s poles | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
6 | Check number of device operating cycles | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
7 | Check spring charging motor charging time at 0.85 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
8 | Check general condition of mechanism | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
9 | Check tripping forces (crescent shaped part) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Breaking Unit (Arc Chutes + Contacts)
10 | Check the filters cleanliness and the attachment of the arc-chute | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
11 | Check condition of breaking unit | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
12 | Measure resistance of input/output contact | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Control Accessories
13 | Check auxiliary wiring and insulation | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
14 | Check operation of indication contacts (OF / PF / MCH) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
15 | Check closing operation of control auxiliary XF | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
16 | Check opening operation of control auxiliary MX at 0.70 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
17 | Check operation of control auxiliary MN/MNR between 0.35 and 0.7 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
18 | Check delay of MNR devices at 0.35 and 0.7 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
19 | Check MX tripping time | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
20 | Check the service life of the accessories XF, MX, MN | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
21 | Preventative replacement of control accessories | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Trip Unit
22 | Trip trip unit using test tool and check operation of contacts SDE and SDE2 | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
23 | Check ground fault protection function (Micrologic 6.0) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
24 | Check tripping curves using test tool, signaling LED (tripped, overload). Save results on PC | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
25 | Check continuity of the tripping chain by primary injection for each phase | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Device Locking
26 | Open and close keylocks installed on device | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
27 | Open and close padlock system installed on device | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Cradle (For Drawout Circuit Breakers)
28 | Remove device from cradle and put it back | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
29 | Check operation of position contacts (CE, CT, CD, EF) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
30 | Check operation of safety shutters | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
31 | Remove dirt and any foreign material, then regrease cradle | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
32 | Regrease disconnecting contact clusters (specific case of corrosive atmosphere) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
33 | Check connection/disconnection torque | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
34 | Clean and regrease racking screw | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Cradle Locking
35 | Open and close keylocks installed on cradle | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
36 | Operate padlocking system | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
Power connections
37 | Check and tighten loose connections | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturers O&M Manual recommended maintenance intervals.
1.5 Electrical Transformer 480/208V
1 | Inspect transformer connections by infrared scanning | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | FHWA Recommended maintenance intervals.
2 | Perform ultrasonic inspection of medium voltage bus supports, insulators, and barriers | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | FHWA Recommended maintenance intervals.
3 | Visually inspect all equipment for unusual conditions | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | FHWA Recommended maintenance intervals.
4 | Test transformer and circuit breaker insulating oil | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | FHWA Recommended maintenance intervals.
Dry-Type (All transformers)
5 | Remove cover and visually inspect all cable/bus connections for evidence of overheating or burning, check for tightness and clean windings | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | O&M Manual recommendation for dry location 1. Perform routine inspections, maintenance, and testing after any severe electrical short circuit, ground fault, or environmental event (e.g., flooding) to determine the operational status of the transformer. 2. Perform the inspections, maintenance and testing if the transformer has been out of service for an extended period of time. Place strip heaters to maintain the transformer temperature above ambient to prevent condensation from forming in the transformer during extended down time.
Liquid-Filled
| Inspect transformers for leaks, deteriorated seals/gaskets, proper oil level, and test oil sample | [6 empty] | X
| Inspect transformer tank and cooling fins for corrosion, chipped paint, dents, and proper connection to ground | [6 empty] | X
| Inspect all bushings for cracks/chips, proper tightness, and evidence of overheating | [6 empty] | X
| Inspect all gauges and alarm devices | [6 empty] | X
| Clean core, coils, and enclosures and inspect any filter | [6 empty] | X
| Perform primary and secondary insulation resistance test where possible | [6 empty] | X
| Perform polarization index test on transformers 500 KVA and larger | [6 empty] | X
| Perform turns ratio tests | [6 empty] | X
| Perform calibration test and verify proper operation of all meters | [6 empty] | X
1.6 Fire Alarm System
1 | Open primary power supply to fire alarm panel and note sounding of trouble alarm and light |  | X |  |  |  | X |  |  |  | Rec. | N | O |  | Elec | FHWA recommendation
2 | Perform fire drill by user of drill switch on fire alarm panels, and check that all visual and audible signal emit a sound and tunnel SCADA system (if any) receives alarm |  | X |  |  |  | X |  |  |  | Rec. | N | O |  | Elec | FHWA recommendation
3 | Clean all smoke and heat detector housings and check battery voltage under load |  |  |  |  | X |  |  |  |  | Rec. | Y |  |  | Elec | FHWA recommendation
4 | Verify that proper alarm devices operate for the appropriate initiating device circuit |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | FHWA recommendation
5 | Check all lamps, alarm devices, and printers for proper operation |  |  |  | X |  | X |  |  |  | Rec. | N | O |  | Elec | FHWA recommendation
6 | Visually inspect control panels | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.1
7 | Visually inspect fire alarm control batteries |  | X |  |  |  | X |  |  |  | Req. | N | O |  | Elec | Per NFPA 72, table 14.3.1
8 | Visually inspect fiber optic connections | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.1
9 | Visually inspect remote annunciators |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.1
10 | Visually inspect duct detectors |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.1
11 | Visually inspect HVAC control dampers |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
12 | Visually inspect tunnel linear heat detectors |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Elec | Per NFPA 72, table 14.3.1
13 | Visually inspect waterflow and tampers |  |  |  | X |  | X |  |  |  | Rec. | Y | O |  | Elec | Manufacturer O&M Manual recommendation
14 | Visually inspect alarm notification appliances |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.1
15 | Visually inspect dialers to remote control center |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
16 | Visually inspect manual fire alarm boxes |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.1
17 | Visually inspect carbon monoxide detectors/systems |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Elec | Per NFPA 72, table 14.3.1
18 | Test control panels | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.2
19 | Test secondary (standby) power supply | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.2
20 | Test UPS (if dedicated to the system used) | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.2
21 | Test manual fire alarm boxes | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Per NFPA 72, table 14.3.2
22 | Test tunnel carbon monoxide detectors/systems | [5 empty] | X |  |  |  | Req. | Y |  |  | Elec | Per NFPA 72, table 14.3.2
23 | Test fire alarm control panel batteries |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation | 2021-09-11 | FACP Batteries: The two FACP batteries that were found to be dead will need to be replaced | Replace the two dead FACP batteries.
24 | Test fiber optic connections | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
25 | Test duct detectors | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
26 | Test HVAC control dampers | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
27 | Test tunnel linear heat detectors | [5 empty] | X |  |  |  | Req. | Y |  |  | Elec | Per NFPA 72, table 14.3.2
28 | Test waterflow and tampers |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
29 | Test dialers to remote control center | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Manufacturer O&M Manual recommendation
1.7 Tunnel Lights
1 | Verify proper operation of the lighting fixtures in the tunnel areas | X |  |  |  |  | X |  |  |  | Rec. | Y | O |  |  | Recommended maintenance intervals by FHWA.
2 | Count and record number of lights out on night lighting and day lighting | X |  |  |  |  | X |  |  |  | Rec. | Y | O | C |  | Recommended maintenance intervals by FHWA. | 2021-09-11 | 1. At the time of inspection, each fixture was found to be operational. A single fixture was found to have a protective film over it. 2. The luminance meter was not operational nor communicating with the lighting contactor panel, with the meter reading “0 CD/m | 1. Remove protective film from the 61st fixture from the south end in the bottom row along west wall of the Southbound mainline. 2. Investigate luminance meters not communicating with lighting contactor panels and repair.
3 | Replace any inoperable components | X |  |  |  |  | X |  |  |  | Rec. | Y | O |  | Elec | Recommended maintenance intervals by FHWA.
4 | Pressure wash clean the exterior of lenses on all lighting fixtures in the tunnel. |  |  |  | X |  | X |  |  |  | Rec. | Y | O |  |  | Recommended maintenance intervals by FHWA.
5 | If required clean interior of lenses |  |  |  | X |  | X |  |  |  | Rec. | Y | O |  | Elec | Recommended maintenance intervals by FHWA.
6 | Perform group replacement for any luminaires that have failed | [5 empty] | X |  |  |  | Rec. | Y |  |  | Elec | Recommended maintenance intervals by FHWA.
7 | Replace real time clock battery for the controller | [8 empty] | X | Rec. | Y |  |  | Elec | Manufacturer O&M Manual recommendation
1.8 SCADA
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | N |  | C |  | Recommended by the consultant. | 2021-09-11 | Check signals from by PLC/SCADA are received for fan operation, CO detection. Confirm that detection is properly relayed through the SCADA system to the Cincinnati Fire Department and ODOT’s TMC. | Re-establish PLC/SCADA for fan operation, CO detection. Confirm detection is properly relayed through the SCADA system to the Cincinnati Fire Department and ODOT’s TMC.
1.9 Soft Starters
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | N |  | C |  | Recommended by the consultant. | 2021-09-11 | Soft starter #3 pilot light is broken | Replace pilot light
1.10 Panelboards
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | N |  | C |  | Recommended by the consultant. | 2021-09-11 | Panelboard S-EM has tape covering exposed bus instead of proper space covers | Replace the taped used on Panelboard S-EM with manufacturer specific filler plates.
1.11 UPS
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | Y |  | C |  | Recommended by the consultant. | 2021-09-11 | The 30 KVA UPS system and associated battery racks appeared in good condition with no notable deficiencies. | None.

## Mechanical
Procedure Description |  | Frequency | [8 empty] | Recommended (Rec.) or Required (Req.) | Tunnel Closure Required? | Responsible Party |  |  | Comments | Fall 2021 Inpsection
|  | Weekly | Monthly | Bi-Monthly | Quarterly | Semi-Annually | Annually | Bi-Annually | Tri-Annually | Quinquennial |  |  | ODOT | Consultant | 3rd Party (Mechanic, Electrician, etc.) |  | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance
2.1 TVS Axial Fans
Axial Fans
1 | Operate fans and motor-operated dampers and listen for unusual noises |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Fans to be operated Monthly, but on-site inspection as described here should only occur Quarterly. Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No unusual noises noted during operations. | None.
2 | Check for undue vibration. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | If present, stop the fan at the earliest opportunity, check impeller for any dirt build-up on the blades, and clean as necessary. Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No undue vibration noted during operations. | None.
3 | Operate fans and motor-operated dampers in all configurations. | [5 empty] | X |  |  |  | Rec. | N |  | C | Mech. | A full SCADA check should be performed. | 2021-09-11 | During the inspection, WSP staff attempted to run the tunnel ventilation system through all emergency ventilation modes via the main tunnel SCADA terminal located in the Lytle tunnel ventilation building. WSP observed during testing that the system did not operate when any of the emergency ventilation modes were initiated at the SCADA terminal. Following this test through the SCADA terminal, WSP attempted initial the emergency ventilation operation by triggering a linear heat detection alarm at the Facility Fire Alarm Control Panel (FACP). This test also failed to initial operation of the emergency ventilation system. It should be noted that all alarms were seen correctly at the tunnel FACP but were not seen at the tunnel SCADA terminal. WSP does not believe this to be a ventilation equipment issue, as all fans and dampers were able to be operated manually at their respective local controllers, in all speeds; and is a SCADA issue. | The Lytle tunnel ventilation system is not operating in any normal or emergency operating modes. This is due to malfunctioning of the ventilation system controls and the tunnel SCADA system. WSP believes that repair / reprogramming / debugging of the ventilation system controls/SCADA system is required to bring the tunnel ventilation system back into working order.
4 | Fans should be inspected to ensure that there is no build-up of dirt or other matter that would cause overheating of the motor or obstruct the impeller track. | [5 empty] | X |  |  |  | Rec. | N |  | C |  | Cleaning can be done with air or, preferably with a soft brush and vacuum. All connections and fastenings – bolts, clamps etc should be checked to ensure nothing is loose. | 2021-09-11 | No build-up of dirt or debris noted. | None.
5 | Check all bolts for tightness. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | The bolts to be checked include, canvas connector, fan housing split, duct transition split, duct transition to actuator, fan vibration isolators. Also included are checking the locking collar bolts between the rotor hub and the shaft: verify to a torque rating of 105 lbs. Impeller blades hub cap bolts: verify to a torque rating of 220 ft-lb. Decoder that is attached to the shaft with a locking collar should be verified to be between 25 and 35 in-lbs torque.
6 | Inspect inside and outside of housing and impeller for wear, deterioration, or build-up of material. | [5 empty] | X |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | Minor surface corrosion on impeller hardware observed | None.
7 | Verify damper interlocks and operates properly through all positions. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 did not open when activated. | Inspect damper 4 and actuator on TV-2; determine the root cause of failure. Replace necessary parts.
8 | The locking collar between the rotor hub and the shaft has locking screws that should be veriﬁed to a torque rating of 105 ft/lb. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech.
9 | The impeller blades are held in place to the hub by cap bolts that should be veriﬁed to a torque rating of 220 ft/lb. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech.
10 | The decoder is attached to the shaft with a locking collar that should be veriﬁed to be between 25-35 inches/lb. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech.
11 | Check steel strength and visually inspect grating for ventilation opening in Lytle Park. | [7 empty] | X |  | Rec. | N |  |  | Mech.
12 | Check air flow measurements in each of the tunnels. | [7 empty] | X |  | Rec. | Y |  | C |  |  | 2021-09-11 | Air flow in tunnel bores sufficient. | None.
Fan Motor
13 | Check and record bearing and winding temperatures. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | If elevated temperature readings are found, investigate equipment condition and/or lubricant condition and level. Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | Temperatures normal, no elevated temperatures noted. | None.
14 | Clean up of fan motor. | [5 empty] | X |  |  |  | Rec. | N |  | C |  | Clear away the dust and dirt on outside surface of enclosure and measure. insulation resistance. | 2021-09-11 | Grease leakage from the back motor bearing on TV-1 and Tv-3 was observed. | Monitor grease leakage.
15 | Check connecting terminals. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Check the connecting bolts (nuts) in terminal box to see whether connecting bolts (nuts) are loose or not. Replace them when necessary. Check the connecting terminals in the terminal box. The connecting terminals in the terminal box should not only be checked for correct tightness but a thermal scan can be taken and printed to verify all crimped terminal ends are correct. The thermal scan will be performed at the end of the day following run testing.
16 | Check the bolts (nuts). | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Check earthing bolts (nuts), fastening bolts on end shield and internal and external bearing covers, connection of ground lead and setting. External bearing cover bolts can be checked on the external and (decoder end), internal (fan shaft end) are obstructed by the fan hub and axial blades (2,000 lbs.) cannot be easily checked.
17 | Check bearing. | [6 empty] | X |  |  | Rec. | N |  |  | Mech. | Dismounting bearing cap, check whether the grease in bearings has been dirty and dried up or not. It should be replenished as required if there is short of grease. Replace the bearings when necessary. High temperature grease must be adopted according to the motor data sheet. The motor bearing cap is attached to the motor casing. The internal (fan shaft end) is obstructed by the fan hub and axial blades (2,000 lbs.) and cannot be easily removed. The external (RPM decoder end) is less difficult but the bearing is pressed into the motor end housing and very little can be accomplished by just inspecting the outer surface. We suggest that the grease be renewed biannually by removal of the bearing relief plug on the bottom of the bearing housing on the motor. Then ﬂush new grease through the bearing until fresh grease is witnessed at the relief port in the capture vessel. This will be performed at a bi-annual frequency.
18 | Check the appearance of motors to see whether it has been damaged. Clear away dust and dirt and repair damaged sections. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Yearly maintenance or overhaul consists of quarterly maintenance or routine repair.
19 | Check windings. | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec. | a) Measure insulation resistance on all live parts with a megger and the insulation resistance value should be larger than 1MΩ.
20 | Bearing purge and grease renewed. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | a) High temperature grease must be adopted according to the motor data sheet. b) The motors are supplied with loose leads. Where a terminal box is fitted, all cable terminations should be tightly secured.
21 | Motor internal space heater: The amp draw should be veriﬁed on the 110V circuit. Record and review record for consistency. | [6 empty] | X |  |  | Rec. | N |  |  | Mech.
22 | Vibration transmitters on fans: test and record amplitude. Review records for consistency and any aberrations. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech.
2.2 Isolation Dampers
Fan Isolation Dampers
1 | Operate motor-operated dampers and listen for unusual noises and vibrations |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Perform operational checkout (including cycle testing – opening and closing the damper a few times under electrical power) and verify position status with the main control panel – This can be waived if dampers are cycled on a daily basis during normal use. Qualified ODOT or consultant staff may perform this function. Mechanical contractor to adjust as required. | 2021-09-11 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 did not open when activated. | Inspect damper 4 and actuator on TV-2; determine the root cause of failure. Replace necessary parts
2 | Check bearings for wear and dampers for debris. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Visual inspection only. Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No deficiencies noted. | None.
3 | Clean damper blades and linkages. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Clean dirt and debris from the damper and actuators.
4 | Visually inspect dampers and actuators for the build up of dirt, debris, wear and corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | In general, the dampers must be kept clean and free from foreign matter that may impede normal movement and/or seating of the blades and seals. Therefore, dampers should be cleaned and inspected for general physical and mechanical condition. This inspection should include checking the mechanical tightness of bolted connections, visual inspection for the buildup of dirt or debris that may prevent damper closure and a general inspection for any obvious maintenance. | 2021-09-11 | No deficiencies noted. | None.
5 | Inspect jamb and blade seals for damage and proper sealing. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
6 | Inspect the dampers for premature corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
7 | Check tightness of mechanical connections |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Manually check all the fasteners to ensure they are still tight. This can be done by checking with hands only. Generally if a fastener is loose, this will be a noticable check. Tighten all fasteners as necessary.
8 | Test internal actuator heater | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Each actuator has an internal heater supplied by a separate 110 volt circuit. These will be tested and amp draw recorded annually to assure proper operation.
Southbound Tunnel Dampers
9 | Operate motor-operated dampers and listen for unusual noises and vibrations. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Perform operational checkout (including cycle testing – opening and closing the damper a few times under electrical power) and verify position status with the main control panel – This can be waived if dampers are cycled on a daily basis during normal use. Qualified ODOT or consultant staff may perform this function. Mechanical contractor to adjust as needed. | 2021-09-11 | No deficiencies noted. | None.
10 | Check bearings for wear and dampers for debris. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No deficiencies noted. | None.
11 | Clean damper blades and linkages. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Clean dirt and debris from the damper and actuators.
12 | Visually Inspect dampers and actuators for the build up of dirt, debris, wear and corrosion |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | In general, the dampers must be kept clean and free from foreign matter that may impede normal movement and/or seating of the blades and seals. Therefore, dampers should be cleaned and inspected for general physical and mechanical condition. This inspection should include checking the mechanical tightness of bolted connections, visual inspection for the buildup of dirt or debris that may prevent damper closure and a general inspection for any obvious maintenance. | 2021-09-11 | No deficiencies noted. | None.
13 | Inspect jamb and blade seals for damage and proper sealing. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
14 | Inspect the dampers for premature corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
15 | Check tightness of mechanical connections |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Manually check all the fasteners to ensure they are still tight. This can be done by checking with hands only. Generally if a fastener is loose, this will be a noticable check. Tighten all fasteners as necessary.
16 | Test internal actuator heater | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | Each actuator has an internal heater supplied by a separate 110 volt circuit. These will be tested and amp draw recorded annually to assure proper operation.
Coffin Dampers (Damper Doors)
17 | Operate motor-operated dampers and listen for unusual noises and vibrations. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Perform operational checkout (including cycle testing – opening and closing the damper a few times under electrical power) and verify position status with the main control panel. Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No unusual noises noted during operations. | None.
18 | Grease bearings using a lithium or lithium complex grease for bearing lubrication. | [5 empty] | X |  |  |  | Rec. | N | O | C |  | Qualified ODOT or consultant staff may perform this function. Flush grease annually and replace.
19 | Chains are to be lubricated with SAE 10W 40 oil. |  |  |  | X |  |  | X |  |  | Rec. | N | O |  | Mech. | Qualified ODOT or consultant staff may perform this function. Check lubrication quarterly - regrease bi-annually.
20 | Visually inspect diversion walls and blades within opening of 3rd street tunnel. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No deficiencies noted. | None.
21 | Strength testing of steel blades in the 3rd street ramp ventilation opening. | [7 empty] | X |  | Rec. | Y |  |  | Mech. | Qualified ODOT or consultant staff may perform this function.
22 | Check actuator performance. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Covers should not be removed during routine maintenance. Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | No deficiencies noted. | None.
23 | Actuator battery replacement. | [7 empty] | X |  | Rec. | N |  |  | Mech. | Refer to ROTORK maintenance manual for procedures. Initial replacement to occur in Spring 2018 as existing life of battery is unknown.
2.3 Carbon Monoxide Detection System
1 | Visual inpection |  |  |  | X | [5 empty] | Rec. | Y | O | C |  | Qualified ODOT or consultant staff may perform this function. | 2021-09-11 | The two north bore air quality monitors were found to have an error message displayed. The air quality monitors in the south bore and south ramp, appeared to be working properly and displayed 0ppm. | The error on the two north bore monitors should be investigated and cleared by a qualified technician. Repairs should be made if determined necessary by the technician.
2 | Zero Calibration. |  |  |  |  | X |  |  |  |  | Rec. | Y |  |  | Mech. | Calibration and maintenance is carried out using a Magnetic Wand, this allows a single user to undertake routine maintenance without needing to access internal components.
3 | Span Calibration |  |  |  |  | X |  |  |  |  | Rec. | Y |  |  | Mech.
4 | Check signal read by PLC/SCADA. |  |  |  |  | X |  |  |  |  | Rec. | Y |  | C |  | Ensure signal read by the SCADA is same as displayed by the CO detectors at each transmitter. | 2021-09-11 | Readings showed up accurately at the tunnel SCADA terminal. | None.
2.4 Standpipe
1 | Fire Department Connections Capped and Clear |  |  |  |  | X |  |  |  |  | Req. | N |  | C |  | NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems outlines the maintenance criteria and testing procedures for a manual dry standpipe. | 2021-09-11 | FDC capped and clear during inspection. | None.
2 | Confirm threads are undamaged and caps in place. |  |  |  |  | X |  |  |  |  | Req. | Y |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
3 | Confirm top nut and caps are tight but not over-torqued. |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Mech.
4 | Operate all control valves by closing and opening low point drains. |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Mech.
5 | Drain all low point drains. |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Mech.
6 | Inspect piping, hose connections and couplings. | [5 empty] | X |  |  |  | Req. | Y |  | C |  |  | 2021-09-11 | During the inspection the standpipe system underwent a hydrostatic test per NFPA 25. The system held pressure at 200psi for 2hrs. The most common standpipe defects observed are listed below. - Corrosion on Fire Hose Valve (FHV) wheel - Missing FHV caps - Unattached FHV cap chains - Corrosion on pipe threads at FHV - Corrosion on 2.5” galvanized branch pipe to FHV - Significant corrosion on standpipe risers, including widespread surface rust and pitting on piping, valves, pipe hangers and couplings. - Pipe labels not long affixed to riser pipes. | 1. Replace all standpipe pipe labels 2. Replace all fire hose valve wheels 3. Replace missing fire hose valve caps 4. Reattach all fire hose valve cap chains
7 | Test flow hydrant. |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Other | This element is the responsibility of the City.
8 | Hydrostatic testing of the system. | [8 empty] | X | Req. | Y |  |  | Mech. | Cincinnati Fire Department should be invited to witness this test.
2.5 Soundproofing
Fan Sound Attenuation
1 | Visually inspect fan sound attenators for the build up of dirt, debris, wear and corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
Soundproofing Boards
2 | Visually inspect fan soundproofing boards for the build up of dirt, debris, wear and corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  |  | 2021-09-11 | No deficiencies noted. | None.
2.6 HVAC
Commercial Electric Unit Heater
1 | Check the tightness of all visible bolts and nuts, in particular the support structure bolts and nuts. Similarly check the motor mounting bolts located in the top and back of the heater case. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Potentially lethal voltages are present. Be sure to lock the branch circuit disconnect switch in the OFF position and tag the circuit “Out for Maintenance” before working on this equipment.
2 | Check the motor, fan, discharge openings, intake openings, heating elements and control compartment for cleanliness. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | If necessary, clean by using a vacuum or compressed air. Be careful not to bend the fan blade propeller.
3 | Check that the electric motors are permanently lubricated and thermally protected. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
4 | Inspect all terminal connections, contactor and conductor insulation for damage, looseness, fraying, etc., as applicable. Tighten any loose terminals and replace or repair wire with damaged or deteriorated insulation. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Badly pitted, welded together, or burned shall be replaced.
Fans
5 | All fasteners should be checked for tightness each time maintenance checks are performed prior to restarting unit. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
6 | Motor maintenance is generally limited to cleaning and lubrication (where applicable). |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
7 | Motors supplied with grease fittings should be greased in accordance with manufacturer’s recommendations. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Where motor temperatures do not exceed 104°F (40°C), the grease should be replaced after 2000 hours of running time as a general rule. All bearings on standard Model BSQ fans are factory lubricated and require no further lubrication under normal use (between -20°F and 180°F in a relatively clean environment).
8 | Belts should be checked periodically for wear and tightness. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | For belt replacement, loosen the tensioning device far enough to allow removal of the belt by hand. Do not force belts on or off. This may cause cords to break, leading to premature belt failure. Once installed, adjust belts as shown in “Pre-Starting Checks.” Replace belts every 2 years.
Dampers
9 | Operate motor-operated dampers and listen for unusual noises and vibrations |  |  |  | X | [5 empty] | Rec. | N |  |  | Mech.
10 | Check bearings for wear and dampers for debris. |  |  |  | X | [5 empty] | Rec. | N |  |  | Mech.
11 | Visually inspect dampers and actuators for the build up of dirt, debris, wear and corrosion. |  |  |  | X | [5 empty] | Rec. | N |  |  | Mech. | a) If cleaning is necessary, use mild detergents or solvents. Clean with a non-oil based solvent. b) If lubrication is desired for components such as axle bearings, jackshaft bearings and jamb seals, do not use oil-based lubricants or any other lubricants that attract contaminants such as dust.
12 | Test smoke dampers. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | They will be cycle tested by voltage drop to assure proper function. They will not be tested through the ﬁre alarm system.
Split-System
13 | Check vertical centrifugal pump. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Ensure pump is automatically starting and stopping and performing as designed.
14 | Pull outdoor unit access door and clean bottom of the unit of dirt or debris. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
15 | Check outdoor coil for cleanliness and clean if needed |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
16 | Check indoor filters, clean and/or change as needed |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
17 | Inspect indoor coil and indoor blower for cleanliness |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
18 | Tighten all electrical connections |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
19 | Check condenser fan blades for tightness |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
20 | Inspect contactor contacts |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
21 | Check and record temperature drop across evaporator coil |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
22 | Inspect overall operation of unit |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
23 | Visual inspection for refrigerant leaks |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
24 | Check “error history" and execute delete error history |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
25 | Select “self check" and confirm no errors existing |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
26 | Execute "test run" and inspect outdoor unit for proper operation |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
27 | Make recommendations of any required repairs |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech.
28 | Carry out a malfunction-diagnosis using the remote controller. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | When a malfunction occurs to air conditioner, both indoor unit and outdoor unit will stop and operation lamp blinks to inform unusual stop.

## Structural
Procedure Description |  | Frequency | [8 empty] | Recommended (Rec.) or Required (Req.) | Tunnel Closure Required? | Responsible Party |  |  | Comments | Fall 2021 Inpsection
|  | Weekly | Monthly | Bi-Monthly | Quarterly | Semi-Annually | Annually | Bi-Annually | Tri-Annually | Quinquennial |  |  | ODOT | Consultant | 3rd Party (Mechanic, Electrician, etc.) |  | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance
Portals
1 | Stone/Veneer Facing Inspection | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect for cracked, separated/leaning veneer, etc on portals and wingwalls with each structural inspection. | 2021-09-11 | Isolated locations of masonry veneer cracked or spalled and isolated locations of mortar failure between the edges of the masonry veneer and the concrete portal with up 1/4" wide gaps between mortar and concrete. Retaining wingwalls with isolated missing stones on masonry veneer. Fourth panel from north portal on Wall 11, masonry veneer leaning up to 4" on north side. Saddle catch plates installed. | Monitor leaning masonry veneer.
2 | Lintel- Concrete area directly over portal. | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect for cracks, spalls, loose concrete over traffic. Remove any loose concrete areas over traffic or near traffic during inspection. | 2021-09-11 | Multiple areas of fiberwrapped patches. On North Portal over right edge line of Nourthbound Mainline roadway, linear heat detection wire support not reinstalled after fiberwrap installation. Wire sagging into vehicular envelope. | Reinstall linear heat detection wire support.
3 | Fence | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Inspect for loose connections, deterioration, sturdiness, etc. | 2021-09-11 | No deficiencies noted. | None.
4 | Capstone | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect for cracks, spalls, loose concrete over traffic. Remove any loose concrete areas over traffic or near traffic during inspection. | 2021-09-11 | South Portal over centerline of Southbound Mainline roadway, 9-1/2" wide delaminated area 6" tall on vertical face and extending 10" onto top horizontal face. | Patch delaminated area on South Portal over Southbound Mainline roadway.
Within Vehicular Tunnels
1 | Tiles |  |  |  |  | X |  |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect all tiles visually. Using a rubber mallet, Sound tiles near all cracks, joints, or other missing tiles. Remove all unsound tiles with a steel headed hammer and/chisel. Consultant to do this during the one structural inspection. ODOT to do this all other occasions. | 2021-09-11 | Areas of unsound tiles removed throughout all three tunnel roadways, specifically at expansion joint locations. Delaminated, cracked, or missing tiles are common along joint headers and at isolated locations between joints. | Monitor tiles adjacent to missing tile locations.
2 | Fireproofing | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect fireproofing (white, untiled areas of wall walls). Sound all areas with cracks. Randommly sound other areas. Only remove if displacement is showing or at the direction of the ODOT Project Manager | 2021-09-11 | Heavy hairline map cracking spaced at 3" to 6" on roof and at 6" to 12" on walls. Isolated locations of delaminated and spalled fireproofing with exposed wire mesh reinforcing. | Monitor firerproofing deterioration.
3 | Barrier | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Inspect for accident damage, spalls, snag points, etc. | 2021-09-11 | Full height hairline cracks spaced at 4'. 54" long by 4" wide by 1/4" deep gouge from impact on east barrer in Northbound Mainline roadway at Station 127+60. Isolated collision scrapes and gouges throughout all barriers. Reflectors mounted to the parapets typically broken or missing. | None.
4 | Wearing Surface | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Visually inspect for cracking, spalling, etc. Notify maintenance staff immediately of any potholes that need patched. | 2021-09-11 | Full width transverse cracks up to 1-1/2" (1/4" typical) at tunnel section expansion joint locations. Isolated gouges up to 3/4" deep. | None.
5 | Joints | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect joints for signs of recent moisture (wetness, staining, etc.), separation or displacement. | 2021-09-11 | Crack sealer in roof joints at expansion joint locations beginning to crack and is missing at isolated locations. Vertical displacement up to 5/8" noted at joint locations. | Monitor crack sealer in roof joints.
6 | Overall Structure | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Much of the structural componenents/concrete are covered by tile, veneer, etc. Inspection overall structure for signs of structural distress or deterioration such as displacmeent, contigious cracking, settlement, spalling, moisture, sinkholes, etc. | 2021-09-11 | The tunnel liners and interior walls exhibit hairline cracks in the tiles and isolated spalls with exposed reinforcing and delaminated areas, typically adjacent to construction and expansion joint locations. Full height vertical cracks up to 1/16" wide were noted in the interior walls between the Southbound Ramp and Southbound Mainline (wedge room area). | Epoxy inject cracks, patch spalled areas, and monitor areas of water leakage.
7 | Miscellaneous overhead items | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Inspect the heat detection wire, conduits, damper doors, and abandoned lane reminder lights to ensure nothing is loose or corroded that could fall onto traffic. | 2021-09-11 | Linear heat detection wire supports at two locations missing/pulled out. Cracked lense on abandoned lane reminder light removed at one location. Abandoned lane reminder light locations checked for connection. | Reinstall linear heat detection wire supports.
Mechanical / Electrical /Fan / Plenum areas
1 | Mechanical / Fan Rooms | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. | 2021-09-11 | Isolated full height hairline cracks in walls. Standing water noted in access room between fan room and mechanical room. | Monitor water.
2 | Electrical Rooms | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. Check for cracking in area immediately around floor hangers (round columns) over tunnel area. | 2021-09-11 | Isolated full height cracks up to 1/16" wide in walls. Crack gauge installed on wall between plenum space and electrical room. | Monitor cracks.
3 | Plenum Space | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. Check for cracking in area immediately around floor hangers (round columns) over tunnel area. | 2021-09-11 | Isolated full height cracks up to 1/16" wide in walls. Crack gauge installed on wall between plenum space and electrical room. No distress noted in roof slab surrounding hangers. Hanger shell pipes have minor surface corrosion at base. | Monitor cracks.
4 | Hallways, stairs, passageways. | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. | 2021-09-11 | Full height spall (17" wide by 1" deep) with active leakage in north wall at west end of hallway from main access stairs. Hallway between fan room and plenum space with heavy mold/mildew smell. Standing water in southeast stairway to plenum space along east wall. Isolated full height cracks up to 1/16" wide in walls. | Epoxy inject/patch spall with leakage. Monitor cracks areas of standing water.