## Electrical
Procedure Description |  | Frequency | [8 empty] | Recommended (Rec.) or Required (Req.) | Tunnel Closure Required? | Responsible Party |  |  | Facilities Contract | Scope/Requirements | Fall 2021 Inpsection |  |  | Spring 2022 Inpsection |  |  | Fall 2022 Inpsection |  |  | Spring 2023 Inpsection |  |  | Fall 2023 Inpsection |  |  | Spring 2024 Inpsection
|  | Weekly | Monthly | Bi-Monthly | Quarterly | Semi-Annually | Annually | Tri-Annually | Biennially | Quinquennial |  |  | ODOT | Consultant | 3rd Party (Mechanic, Electrician, etc.) |  |  | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance
1.1 Tunnel Closed Notification/Closed Circuit TV | [16 empty] | Manufacturers O&M Manual for CCTV - Not Provided.
1 | Clean, align, and focus all cameras after tunnel washing |  |  |  |  | X |  |  |  |  | Rec. | Y | O |  |  | no | Recommended maintenance intervals by FHWA. |  |  |  | 2022-03-31 |  |  |  | no comments
2 | Test tunnel closed notification system | [5 empty] | X |  |  |  | Rec. | Y |  |  | Elec | no | Recommended maintenance intervals by ODOT. |  |  |  | 2022-04-01 |  |  | 2022-10-01 | The tunnel closed notification system was tested, and no deficiencies were noted |  |  | Not noted in summary |  | 2024-10-01 | ok
1.2 Emergency Lighting - Buildings
1 | Operate test buttons on emergency light fixtures |  | X |  |  | X |  |  |  |  | Req. | N | O |  | Elec | Yes | Per NFPA 101, section 7.9.3 : 1) functional testing to be conducted every 3 to 5 weeks (beyond 30 days to be approved by AHJ) OR 2) self-testing/self diagnosticbattery-operated automatic test once every 30 days for 30 seconds. A visual inspection at invervals not exceeding 30 days OR 3) Computer-based, self-testing/self-diagnostic battery-operated, automatic test not less than every 30 days for a minumum of 30 seconds. | 2022-10-01 | Emergency lighting excercised by Glenwood from local "Test" buttons. No deficiencies noted. | None | 2022-03-31 |  |  | 2022-10-01 | the emergency tunnel lighting system was functionally tested via the lighting control panels and exhibited no notable deficiencies. |  | 2023-04-13 | Emergency lighting inside tunnel control building was tested; Emergency egress lamps need replaced. No issues noted otherwise |  | 2024-10-01 | ok
2 | Operate battery pack for emergency lighting for 90 minutes | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 101, section 7.9.3 : 1) if the emergency lighting system is self-testing/self-diagnostic, then the equipment shall be fully operation for the duration of the 90 minutes test OR 2) if the system if computer-based, then the 90 minutes test shall be performed automatically. |  |  |  | 2022-03-31 |  |  | 2022-10-01 | the 2 FACP batteries were found to measure less than 20 AH and need to be replaced. |  | 2023-04-13 | Emergency lighting inside tunnel control building was tested; Emergency egress lamps need replaced. No issues noted otherwise |  | 2024-10-01 | ok
1.3 Electrical Switchboard and Switchgear | [16 empty] | Recommended maintenance intervals by FHWA:
1 | Inspect switchgear bus and connections by infrared scanning | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | No | Manufacturers O&M Manual recommendations: On the circuit breaker molded case there should not be: 1) no traces of grime (grease), excessive dust or condensation which all reduce insulation. 2) no signs of burns or cracks which could weaken the case and thus its capacity to withstand short-circuits. Preventative maintenance recommendation for molded case: 1) A visual inspection of its condition and cleaning with a dry cloth or a Q14vacuum cleaner. All cleaning products with solvents Q14are strictly forbidden. 2) Measuring the insulation every five years and following trips due to a short-circuit. Replace the circuit breaker if there are signs of burns or cracks. The arc chutes must be regularly checked. The fins of the arc chutes may be blackened (due to the gases produced at In) but must not be significantly damaged. What is more, the filters must not be blocked to avoid internal overpressures. Use a vacuum cleaner rather than a cloth to remove dust from the outside of the arc chutes. Regular operation is required to maintain the normal performance level of each part involved in the opening and closing cycles. In installations where power circuit breakers are used in source changeover systems, it is advised to periodically operate the circuit breaker for the alternate source. Preventative maintenance for MX and XF shunt releases and MN undervoltage release consists of periodically cheaking operation at minimum values. Auxiliary wiring must be regularly checked and replaced as needed, particularly if there are vibrations, high ambient temperatures or corrosive atmospheres. Periodic checks on the spring charging motor operation and the charging time are required to ensure the device function. To ensure correct operation of electronic trip unit, it is necessary to periodically check: • the chain of action resulting in a trip • the response time as a function of the level of the fault current. Periodic checks on the orders (read, write, commands) transmitted by the communication bus are required to maintain a high degree of reliability and confidence in the communication system. If fixed circuit breaker connections are not made with Schneider Electric recommendations (tightening torque, hardware, and contact washer), then regularly check the temperature-rise points. If there is a change in color of copper or tinning: • dismantle the connections • clean and scrape the contact surfaces • then reassemble the connections using new hardware. Check the terminals. Drawout circuit breakers connections require periodic cleaning. Always inspect the switchboard after a fault. General switchboard inpsection and cleaning: 1. Vacuum the switchboard interior to remove any dirt or dust deposits. Wipe all bus bars, insulators, cables, etc., with a clean, dry, lint-free cloth. 2. Check the switchboard interior carefully for moisture, condensation build-up, or signs of any previous wetness. Inspect all conduit entrances and cracks between the enclosure panels for dripping leaks. Take the necessary steps to eliminate the moisture and seal off all leaks. 3. Inspect the switchboard for any signs of overheating. Discoloration and flaking of insulation or metal parts are indications of overheating. 4. Check for signs of rodent nesting in the switchboard. 5. Carefully inspect all devices for any visibly worn-out, cracked, or missing parts. 6. Manually open and close switches and circuit breakers several times to verify they are working properly. 7. Verify that all key interlocks and door interlocking provisions are working properly. Bus Bar Joints, Lug Terminations, and Insulating Materials 1. Bus bar joints are maintenance-free. Do not retighten them after the pre-energizing checkout procedure is complete. 2. Check all bus bar joints and terminal lugs for any pitting, corrosion, or discoloration resulting from high temperatures or subjection to high fault conditions. If any damage has occurred, replace the bus bars or lugs. If cleaning is required, use Lectra-Clean®, made by CRC. 3. Inspect all insulating materials. Before re-energizing the switchboard, replace insulators with any visible damage (such as cracks). Bolt-Loc switch maintenance: 1. Exercise the operating mechanism at least once a year to ensure proper operation. 2. The Bolt-Loc switch is shipped from the factory properly lubricated. Periodic cleaning and lubrication of the switch is required. The maintenance interval between lubrications depends on factors such as usage and ambient conditions. The maximum recommended maintenance interval is one year for current-carrying parts and five years for operating mechanisms. Exercise circuit breakers at least once a year to ensure proper operation. For general maintenance: 1. Trip the circuit breaker by pushing the Push-To-Trip or “Open” button located on the face of the circuit breaker. Refer to the appropriate circuit breaker manual for the specific location of this button. 2. Manually open and close the circuit breaker two to three times. QMB/QMJ/QMQB1 Fusible Switches 1. Periodically exercise the switch to ensure proper operation. This period should not exceed one year. 2. Check the cover interlock with the switch in the ON position. The cover should not open using normal hand force. 3. Inspect the switch interior for any damaged or cracked parts, and replace as necessary. 4. For fusible switch units, check the fuse mounting clips or bolted contact area for corrosion or discoloration (indicating overheating). Replace them if necessary. 5. For additional maintenance instructions, see the label on the inside of the door. After the equipment in switchgear has been lubricated, perform the following steps. 1) Inspect all components for cracks, loose parts, and weather or chemical damage. 2) If cracks or strain damage are suspected, remove the unit from service. If cracked components are detected, replace them before returning unit to use. 3) Periodically check for distortion of the traveling lifter. If distortion is found: — Verify that the rails and sections are aligned. — Verify that the carriage and winch mechanism have been installed correctly. — Verify that the cable has been fastened securely to the winch drum. — Verify that the gears are well lubricated. NOTE: For normal operation, use a heavy gear lubricant. In very dirty or gritty conditions, it is advisable to use a dry lubricant such as dry graphite to lubricate the gears. Never allow the gears to run dry. 4) If applicable, remove handling means and any obstructions from the top of the unit that could inhibit operation of the traveling lifter. 5) Thoroughly inspect the traveling lifter wire cable. Pay close attention to cable sections, such as parts passing over sheaves or wound on the drum, which are normally hidden during inspection or maintenance procedures.Contact Schneider Electric Services at 1-888-778-2733 if the cable shows any of the following signs of deterioration: — Kinking, crushing, cutting, or unstranding — Corroded, cracked, bent, or broken wires — Worn end connections 6) Always keep the exterior finish in good condition to protect against corrosive damage. When damage is noticed, remove the finish to bare metal and refinish using a high-quality primer and finish coat. 7) Be certain that all the warning labels are still in place and readable. If the warning labels become unreadable or are destroyed, contact your local Schneider Electric sales office. 8) Do not repair any parts that are worn, cracked, deformed, misaligned, or severely corroded. Repairing parts does not ensure satisfactory or safe performance. Do not substitute other manufacturers’ parts. 9) Record all inspections and maintenance performed on the traveling lifter in a maintenance log. Inspect the SPD periodically to maintain reliable system performance and continued transient voltage surge suppression. Periodically check the state of the diagnostic display panel LED status indicators. Routinely use the built-in diagnostics to inspect for inoperative modules. | [6 empty] | 2022-10-01 | Document dated April 4, 2022 from Electircal Certification Incorporated, determined "no issues" noted. |  | 2023-04-13 | Switchgear and distribution equipment was tested and cleaned by ECI and Glenwood Electric. There is a tie breaker transfer issue that has risen that Glenwood will address when return from vacation. No issues noted otherwise. |  | 2024-10-01 | ok
2 | Perform ultrasonic inspection of medium voltage switchgear bus supports, insulators, and barriers | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | [7 empty] | 2022-10-01 | Document dated April 4, 2022 from Electircal Certification Incorporated, determined "no issues" noted. |  |  |  |  | 2024-10-01 | ok
3 | Visually inspect all equipment for unusual conditions | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Yes | [7 empty] | 2022-10-01 | Document dated April 4, 2022 from Electircal Certification Incorporated, determined "no issues" noted. |  | 2023-04-13 |  |  | 2024-10-01 | ok
4 | Check tightness of all connections | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Document dated April 4, 2022 from Electircal Certification Incorporated, determined "no issues" noted. |  | 2023-04-13 |  |  | 2024-10-01 | ok
5 | Review results of last visual, infrared, and ultrasonic inspection | [6 empty] | X |  |  | Rec. | N |  | C |  | Yes |  | 2021-09-11 | Infrared inspection was performed on each piece of elec equip and no deficiencies were found. | N/A |  |  |  | 2022-10-01 | Results reviewed in inspection report |  |  |  |  | 2024-10-01 | ok
6 | After power shutdown, clean entire switchgear interior | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Swithgear cleaned per April 4, 2022 Electrical Certification Inc document |  | 2023-04-13 | Switchgear and distribution equipment was tested and cleaned by ECI and Glenwood |  | 2024-10-01 | Switchgear and distribution equipment was tested and cleaned by ECI and Glenwood
7 | Clean all bus insulators and check for cracks and chips | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed and noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok
8 | Clean, lubricate (if applicable), and verify operation of all control switches, auxiliary relays, and devices | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed and noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok
9 | Clean, lubricate, adjust, and add anti-oxidant grease to contacts of all disconnect switches | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed and noted in inspection report |  |  |  |  | 2024-10-01 | ok
10 | Clean and perform insulation resistance testing on all lighting arrestors | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed and noted in inspection report |  |  |  |  | 2024-10-01 | ok
11 | Perform insulation resistance testing on any bus bars | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed and noted in inspection report |  |  |  |  | 2024-10-01 | ok
12 | Perform calibration test and verify proper operation of all meters | [6 empty] | X |  |  | Rec. | N |  |  | Elec | Yes |  |  |  |  | 2022-03-31 |  |  | 2022-10-01 | Task performed and noted in inspection report |  |  |  |  | 2024-10-01 | ok
Low Voltage Air Circuit Breakers
13 | Remove covers and thoroughly clean each breaker and contact surfaces | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed and noted in inspection report |  |  |  |  | 2024-10-01 | ok
14 | Apply anti-oxidant grease to breaker's main contacts | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | This is not identified in inspection report |  |  |  |  | 2024-10-01 | ok
15 | Lubricate and verify opeation of all mechanisms | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | This is not identified in inspection report |  |  |  |  | 2024-10-01 | ok
16 | Apply current equal to 90 to 110 percent of the breaker trip coil setting to verify proper pick-up of tripping mechanism | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Vent Fan#1 trip unit not responding with test unit |  |  |  |  | 2024-10-01 | Vent Fan #2 Low Speed soft starter was found to frequently trip offline with a “Phase Fault” error, disabling the fan until manually reset by maintenance personnel
17 | Record trip times for long-time, short-time instaneous, and ground fault breakers when passing loads equal to multiples of their listed ratings through each phase of the breaker | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | This is not identified in inspection report |  |  |  |  | 2024-10-01 | ok
18 | Measure contact resistance and adjust where possible | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Contact resistance measured |  |  |  |  | 2024-10-01 | ok
19 | Perform and record results of insulation resistance test from each pole to other two poles and to ground | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Insulation resistance results not recorded |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
20 | Clean and lubricate breaker carriage and racking mechanism on any draw out breakers | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Draw out breaker "vent fan 1" in main switchgear has non-functional LCD on micrologic trip unit |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Modled Case Circuit Breakers
21 | Inspect breaker for proper installation | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed no issues |  |  |  |  | 2024-10-01 | the automatic tie breaker control for the facility is non-functional and the facility appears to be experiencing utility service reliability issues. | Monitor both incoming utility sources reliability | 2024-10-01 | the automatic tie breaker control for the facility is non-functional and the facility appears to be experiencing utility service reliability issues. | Monitor both incoming utility sources reliability
22 | Remove cover (if possible) and fully clean interior and exterior | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
23 | Inspect for burning, overheating, wear, and proper alighment | [6 empty] | X |  |  | Rec. | N |  |  | Elec | Yes |  |  |  |  | 2022-03-31 |  |  |  | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
24 | Perform contact resistance and insulation resistance measurements and test | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [7 empty] | 2022-10-01 | Task performed no issues |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
25 | Apply current equal to 300 percent of breaker rating to test the long-time element | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | 0k |  | 2024-10-01 | 0k
26 | Test and compare any breakers with instantaneous trip units to manufacturer's characteristic curve | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Automatic Transfer Switch (600 Volt Class)
27 | After total outage is obtained, clean all contact surfaces, apply anti-oxidant contact grease, measure and record contact resistance, and make any adjustments if necessary | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
28 | Lubricate bearings, links, pins, and cams | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
29 | Perform insulation resistance test | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Results not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
30 | Test all settings of voltage, frequency sensing, and timing relays | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Low Voltage Insulated Cable (Less Than 600 Volts)
31 | Check all cable terminations for tightness | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
32 | Perform and record results of insulation resistance test from each phase to the other two and to ground for one minute using a test voltage of 1,000 volts Direct Current (DC). Compare results with previous test. | [6 empty] | X |  |  | Rec. | N |  |  | Elec | No | [8 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
1.4 Masterpact NT and NW Circuit Breakers
Case
1 | Measure insulation resistance | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Results not recorded in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Device
2 | Check the general condition of the device (accessory cover, trip unit, case, cradle, connections) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | No | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Mechanism
3 | Open/close device manually and electrically | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
4 | Charge device electrically | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
5 | Check complete closing of device’s poles | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
6 | Check number of device operating cycles | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
7 | Check spring charging motor charging time at 0.85 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
8 | Check general condition of mechanism | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
9 | Check tripping forces (crescent shaped part) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Breaking Unit (Arc Chutes + Contacts)
10 | Check the filters cleanliness and the attachment of the arc-chute | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
11 | Check condition of breaking unit | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report
12 | Measure resistance of input/output contact | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Control Accessories
13 | Check auxiliary wiring and insulation | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
14 | Check operation of indication contacts (OF / PF / MCH) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
15 | Check closing operation of control auxiliary XF | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
16 | Check opening operation of control auxiliary MX at 0.70 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
17 | Check operation of control auxiliary MN/MNR between 0.35 and 0.7 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
18 | Check delay of MNR devices at 0.35 and 0.7 of rated voltage | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
19 | Check MX tripping time | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
20 | Check the service life of the accessories XF, MX, MN | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
21 | Preventative replacement of control accessories | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Trip Unit
22 | Trip trip unit using test tool and check operation of contacts SDE and SDE2 | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
23 | Check ground fault protection function (Micrologic 6.0) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
24 | Check tripping curves using test tool, signaling LED (tripped, overload). Save results on PC | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
25 | Check continuity of the tripping chain by primary injection for each phase | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Device Locking
26 | Open and close keylocks installed on device | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
27 | Open and close padlock system installed on device | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Cradle (For Drawout Circuit Breakers)
28 | Remove device from cradle and put it back | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
29 | Check operation of position contacts (CE, CT, CD, EF) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
30 | Check operation of safety shutters | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
31 | Remove dirt and any foreign material, then regrease cradle | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
32 | Regrease disconnecting contact clusters (specific case of corrosive atmosphere) | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
33 | Check connection/disconnection torque | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
34 | Clean and regrease racking screw | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Cradle Locking
35 | Open and close keylocks installed on cradle | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
36 | Operate padlocking system | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Power connections
37 | Check and tighten loose connections | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | Manufacturers O&M Manual recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
1.5 Electrical Transformer 480/208V
1 | Inspect transformer connections by infrared scanning | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | FHWA Recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
2 | Perform ultrasonic inspection of medium voltage bus supports, insulators, and barriers | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | FHWA Recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
3 | Visually inspect all equipment for unusual conditions | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | FHWA Recommended maintenance intervals. |  |  |  | 2022-03-31 |  |  |  | Not noted in inspection report
4 | Test transformer and circuit breaker insulating oil | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | FHWA Recommended maintenance intervals. | [7 empty] | Not noted in inspection report |  |  |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
Dry-Type (All transformers)
5 | Remove cover and visually inspect all cable/bus connections for evidence of overheating or burning, check for tightness and clean windings | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | no | O&M Manual recommendation for dry location 1. Perform routine inspections, maintenance, and testing after any severe electrical short circuit, ground fault, or environmental event (e.g., flooding) to determine the operational status of the transformer. 2. Perform the inspections, maintenance and testing if the transformer has been out of service for an extended period of time. Place strip heaters to maintain the transformer temperature above ambient to prevent condensation from forming in the transformer during extended down time. |  |  |  | 2022-03-31 |  |  |  | Not noted in inspection report
Liquid-Filled
| Inspect transformers for leaks, deteriorated seals/gaskets, proper oil level, and test oil sample | [6 empty] | X
| Inspect transformer tank and cooling fins for corrosion, chipped paint, dents, and proper connection to ground | [6 empty] | X
| Inspect all bushings for cracks/chips, proper tightness, and evidence of overheating | [6 empty] | X
| Inspect all gauges and alarm devices | [6 empty] | X
| Clean core, coils, and enclosures and inspect any filter | [6 empty] | X
| Perform primary and secondary insulation resistance test where possible | [6 empty] | X
| Perform polarization index test on transformers 500 KVA and larger | [6 empty] | X
| Perform turns ratio tests | [6 empty] | X
| Perform calibration test and verify proper operation of all meters | [6 empty] | X
1.6 Fire Alarm System
1 | Open primary power supply to fire alarm panel and note sounding of trouble alarm and light |  | X |  |  |  | X |  |  |  | Rec. | N | O |  | Elec | no | FHWA recommendation |  | See protegis test report |  | 2022-03-31 |  |  | 2022-10-01 | no issues noted |  | 2023-04-13 | All components of the fire alarm system were inspected and tested. No issues noted. |  | 2024-10-01 | All components of the fire alarm system were inspected and tested. No issues noted. |  | 2024-10-01 | All components of the fire alarm system were inspected and tested. No issues noted.
2 | Perform fire drill by user of drill switch on fire alarm panels, and check that all visual and audible signal emit a sound and tunnel SCADA system (if any) receives alarm |  | X |  |  |  | X |  |  |  | Rec. | N | O |  | Elec | no | FHWA recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | cannot be performed until SCADA is updated |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
3 | Clean all smoke and heat detector housings and check battery voltage under load |  |  |  |  | X |  |  |  |  | Rec. | Y |  |  | Elec | no | FHWA recommendation |  | See protegis test report | [5 empty] | Not noted in inspection report
4 | Verify that proper alarm devices operate for the appropriate initiating device circuit |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | no | FHWA recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
5 | Check all lamps, alarm devices, and printers for proper operation |  |  |  | X |  | X |  |  |  | Rec. | N | O |  | Elec | no | FHWA recommendation | 44835 | Heat detectors have analog heat sensor element, but the cast junction box covers are missing. | Furnish and install sixteen (16) thermal heat detector junction box covers | 2022-03-31 |  |  | 2022-10-01 | no issues |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
6 | Visually inspect control panels | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
7 | Visually inspect fire alarm control batteries |  | X |  |  |  | X |  |  |  | Req. | N | O |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  | 2022-10-01 | fire alarm control checked; no issues |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
8 | Visually inspect fiber optic connections | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
9 | Visually inspect remote annunciators |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
10 | Visually inspect duct detectors |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
11 | Visually inspect HVAC control dampers |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
12 | Visually inspect tunnel linear heat detectors |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
13 | Visually inspect waterflow and tampers |  |  |  | X |  | X |  |  |  | Rec. | Y | O |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  | 2022-10-01 | no issues noted |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
14 | Visually inspect alarm notification appliances |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
15 | Visually inspect dialers to remote control center |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
16 | Visually inspect manual fire alarm boxes |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
17 | Visually inspect carbon monoxide detectors/systems |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Elec | Yes | Per NFPA 72, table 14.3.1 |  | Inspect Carbon Monoxide Sensors have been reset and initiavi Fan Control de mitigavi inspect CO |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 | Calibrated and bump tested all 8 CO Sensors in the tunnels and control building. Verified proper operation and correct readings at the SCADA system. |  | 2024-10-01 | Calibrated and bump tested all 8 CO Sensors in the tunnels and control building. Verified proper operation and correct readings at the SCADA system. |  | 2024-10-01 | Calibrated and bump tested all 8 CO Sensors in the tunnels and control building. Verified proper operation and correct readings at the SCADA system.
18 | Test control panels | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.2 |  | See protegis test report |  | 2022-03-31 |  |  | 2022-10-01 | noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
19 | Test secondary (standby) power supply | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.2 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
20 | Test UPS (if dedicated to the system used) | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.2 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 | UPS and it's associated transfer switch were inspected and operated without issue. |  | 2024-10-01 | UPS and it's associated transfer switch were inspected and operated without issue. |  | 2024-10-01 | UPS and it's associated transfer switch were inspected and operated without issue.
21 | Test manual fire alarm boxes | [5 empty] | X |  |  |  | Req. | N |  |  | Elec | Yes | Per NFPA 72, table 14.3.2 |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
22 | Test tunnel carbon monoxide detectors/systems | [5 empty] | X |  |  |  | Req. | Y |  |  | Elec | Yes | Per NFPA 72, table 14.3.2 |  | Tunnel Carbon Monoxide Sensors have been reset and initiate Fan Control to mitigate tunnel CO |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 | Calibrated and bump tested all 8 CO sensors in tunnels and control building. Verified proper operation and correct readings at the SCADA. |  | 2024-10-01 | Calibrated and bump tested all 8 CO sensors in tunnels and control building. Verified proper operation and correct readings at the SCADA. |  | 2024-10-01 | Calibrated and bump tested all 8 CO sensors in tunnels and control building. Verified proper operation and correct readings at the SCADA.
23 | Test fire alarm control panel batteries |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation | 2021-09-11 | FACP batteries; the two FACP batteries found to be dead need replaced | Replace the 2 dead FACP batteries | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 | All components of the fire alarm system were inspected and tested. No issues noted. |  | 2024-10-01 | All components of the fire alarm system were inspected and tested. No issues noted. | Fire Alarm Panel two (2) batteries (only 18-amp hours), NB LHD Monitor Module Junction Box two (2) small batteries, SB LHD Monitor Module Junction Box two (2) small batteries, and Ramp E LHD Monitor Module Junction Box two (2) small batteries need to be replaced. | 2024-10-01 | All components of the fire alarm system were inspected and tested. No issues noted. | Fire Alarm Panel two (2) batteries (only 18-amp hours), NB LHD Monitor Module Junction Box two (2) small batteries, SB LHD Monitor Module Junction Box two (2) small batteries, and Ramp E LHD Monitor Module Junction Box two (2) small batteries need to be replaced.
24 | Test fiber optic connections | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
25 | Test duct detectors | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
26 | Test HVAC control dampers | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
27 | Test tunnel linear heat detectors | [5 empty] | X |  |  |  | Req. | Y |  |  | Elec | Yes | Per NFPA 72, table 14.3.2 |  | LHD Panels are reporting to the FACP, however, the LHD Panels are not reporting to the SCADA PLC downstairs. It could be that the LHD Panel gateway and/or ethernet switch have the wrong IP address. | Resolve LHD Panel Gateway IP addresses, Modbus TCP/IP issues and re-test the six LHD Fire Zones to the SCADA PLC. | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
28 | Test waterflow and tampers |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
29 | Test dialers to remote control center | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec | Yes | Manufacturer O&M Manual recommendation |  | See protegis test report |  | 2022-03-31 |  |  |  | Not noted in inspection report |  | 2023-04-13 |  |  | 2024-10-01 | ok |  | 2024-10-01 | ok
1.7 Tunnel Lights
1 | Verify proper operation of the lighting fixtures in the tunnel areas |  | X |  |  |  | X |  |  |  | Rec. | Y | O |  |  | No | Original design consultant stated FHWA recommends weekly checks. ODOT's practice for all lighting is to perform monthly checks by lighting staff and bi-weekly checks of the roadway which would also identify more serious lighting issues by the County Manager. |  |  |  | 2022-04-01 |  |  | 2022-10-01 | lighting fixtures checked |  | 2023-04-13 | Tunnel lighting controls were inspected and tested for all three tunnels. No issues noted. |  | 2024-10-01 | Tunnel lighting controls were inspected and tested for all three tunnels. No issues noted. |  | 2024-10-01 | Tunnel lighting controls were inspected and tested for all three tunnels. No issues noted.
2 | Count and record number of lights out on night lighting and day lighting |  | X |  |  |  | X |  |  |  | Rec. | Y | O | C |  | No | Recommended maintenance intervals by FHWA. | 2021-09-11 | 1. At the time of inspection, each fixture was found to be operational. A single fixture was found to have a protective film over it. 2. The luminance meter was not operational nor communicating with the lighting contactor panel, with the meter reading “0 CD/m | 1. Remove protective film from the 61st fixture from the south end in the bottom row along west wall of the Southbound mainline. 2. Investigate luminance meters not communicating with lighting contactor panels and repair. | 2022-03-31 |  |  | 2022-10-01 | All fixtures operational at time of inspection.
3 | Replace any inoperable components |  | X |  |  |  | X |  |  |  | Rec. | Y | O |  | Elec | No | Recommended maintenance intervals by FHWA. |  |  |  | 2022-03-31 |  |  | 2022-10-01 | Glenwood repaired north portal Luminance Meter, replaced 3A fuse within enclosure on pole.
4 | Pressure wash clean the exterior of lenses on all lighting fixtures in the tunnel. |  |  |  | X |  | X |  |  |  | Rec. | Y | O |  |  | No | Recommended maintenance intervals by FHWA. |  |  |  | 2022-03-31 |  |  | 2022-10-01 | lenses cleaned |  | 2023-03-30 | All three tunnels were pressure washed for Spring 2023 cleaning |  | 2024-10-01 | All three tunnels were pressure washed for fall 2023 cleaning |  | 2024-10-01 | All three tunnels were pressure washed for fall 2023 cleaning
5 | If required clean interior of lenses |  |  |  | X |  | X |  |  |  | Rec. | Y | O |  | Elec | No | Recommended maintenance intervals by FHWA. |  |  |  | 2022-03-31 |  |  |  | interior lenses do not need cleaned at this time
6 | Perform group replacement for any luminaires that have failed | [5 empty] | X |  |  |  | Rec. | Y |  |  | Elec | No | Recommended maintenance intervals by FHWA. | [7 empty] | this was not noted in inspection report | [5 empty] | this was not noted in inspection report |  |  | this was not noted in inspection report
7 | Replace real time clock battery for the controller | [8 empty] | X | Rec. | Y |  |  | Elec | no | Manufacturer O&M Manual recommendation | [7 empty] | this was not noted in inspection report | [5 empty] | this was not noted in inspection report |  |  | this was not noted in inspection report
1.8 SCADA
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | N |  | C |  | Yes | Recommended by the consultant. | 2021-09-11 | Check signals from by PLC/SCADA are received for fan operation, CO detection. Confirm that detection is properly relayed through the SCADA system to the Cincinnati Fire Department and ODOT’s TMC. | Re-establish PLC/SCADA for fan operation, CO detection. Confirm detection is properly relayed through the SCADA system to the Cincinnati Fire Department and ODOT’s TMC. | 2022-04-01 |  | New SCADA system installed 2022; Updates on machines to be installed and staff training for purpose of remote monitoring of the Lytle Tunnel SCADA system to be completed Fall 2022 | 2022-10-01 | LHD panels are reporting to the FACP, however, the LHD Panels are not reporting to the SCADA PLC downstairs. LHD detection is not properly relayed through the SCADA system to the Cincinnati Fire Department and ODOT's TMC. | Resolve LHD panel Gateway IP addresses, Modbus TCP/IP issues and re-test the six LHD fire zones to the SCADA PLC. Confirm LHD detection is properly relayed thru the SCADA system to Cincinnati Fire Dept and ODOT TMC. Revise SCADA HMI home screen to guide Fire Dept to Emergency Mode screen (RED Highlight Box) and instructions to press "Manual" button, the "Auto" button, then "Auto Cycle" button. Revise SCADA HMI fan control screen to guide fire department to emergency mode screen (RED highlited box) Revise SCADA HMI emergency mode screen to include instructions to fire department; on the following (red highlited boxes) a.) What to expect once one of the six emergemcy mode buttons is pushed, ie. how many fan dampers have to open, how many tunnel dampers have to open and how long it will take before Fan #1 turns on low speed. Then describe how long before Fan #1 turns on high speed. Then describe how long before fan #2 turns on low speed, then hi speed, then fan #3, etc. b.) Time counters for each step so that the fire department can see how many seconds to go before the next fan turns on. | 2023-04-13 | SCADA system was inspected and operated in mock emergency sequences. All components functioned properly with the exception of one of the Northbound Coffin Dampers. (Repairs were taking place). Glenwood will check it's operation when return from vacation. |  | 2024-10-01 | Engage Actemium to add the 8-hour timer to the SCADA Auto Mode/Manual Mode on the Ventilation Fan Control. ScreenEngage Johnson Controls to replace the Fire Alarm Panel and Monitor Module Panel BatteriesEngage Johnson Controls to revise the Tunnel Ventilation Emergency Operations Mode Table on project drawing 133 of 296.Engage Glenwood Electric to label NB and SB Tunnel Portal Jet Fan Control Boxes to read, “Not in Service”. |  | 2024-10-01 | Engage Actemium to add the 8-hour timer to the SCADA Auto Mode/Manual Mode on the Ventilation Fan Control. ScreenEngage Johnson Controls to replace the Fire Alarm Panel and Monitor Module Panel BatteriesEngage Johnson Controls to revise the Tunnel Ventilation Emergency Operations Mode Table on project drawing 133 of 296.Engage Glenwood Electric to label NB and SB Tunnel Portal Jet Fan Control Boxes to read, “Not in Service”.
2 | Check how many clicks it takes for Fire Dept to get to one of the Six Emergency Fan Ventilation Modes | [22 empty] | 2022-10-01 | Six (6) clicks to get one of the six Emergency Fan Ventilation Modes: Scree hit "Fan Control"; 1.) Home; 2) Fan Control Screen hit "Manual"; 3) Fan Control Screen hit "Auto" ; 4) Fan Control Screen hit "Auto Cycle" ; 5) Fan Control Screen hit "Emergency Mode"; 6) Emergency Mode Screen hit "NB Tunnel Emergency Mode (exhaust) or NB Tunnel Emergency Mode (Supply) or "SB Ramp Tunnel Emergency Mode (supply) or SB Ramp Tunnel Emergency Mode (Exhaust)" or SB Tunnel Emergency Mode (Supply) or SB Tunnel Emergency Mode (Exhaust)"
Yes
1.9 Soft Starters
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | N |  | C |  |  | Recommended by the consultant. | 2021-09-11 | Soft starter #3 pilot light is broken | Replace pilot light | 2022-03-31 |  |  | 2022-10-01 | Soft starter #3 has defective "high run" output. Local indicator does not illuminate and SCADA does not receive running status when in high. | Troubleshoot defective starter control and repair. | 2023-04-13 | Soft starters were inspected and operated in both directions. No issues noted. |  | 2024-10-01 | Soft starters were inspected and operated in both directions. No issues noted. | None | 2024-10-01 | Soft starters were inspected and operated in both directions. No issues noted. | None
1.10 Panelboards
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | N |  | C |  |  | Recommended by the consultant. | 2021-09-11 | Panelboard S-EM has tape covering exposed bus instead of proper space covers | Replace the taped used on Panelboard S-EM with manufacturer specific filler plates. | 2022-03-31 |  |  | 2022-10-01 | Panelboard S-EM has tape covering exposed bus instead of proper space covers | Replace the tape used on panelboard S-EM with manufacturer specific filler plates. | 2023-04-13 | Panelboards were inspected and breakers checked and tightened. No issues noted. |  | 2024-10-01 | Panelboards were inspected and breakers checked and tightened. No issues noted. | None | 2024-10-01 | Panelboards were inspected and breakers checked and tightened. No issues noted. | None
1.11 UPS
1 | Visually inspect equipment and verify functionality | [5 empty] | X |  |  |  | Rec. | Y |  | C |  |  | Recommended by the consultant. | 2021-09-11 | The 30 KVA UPS system and associated battery racks appeared in good condition with no notable deficiencies. |  | 2022-03-31 |  |  | 2022-10-01 | The 30 KVA UPS system and associated battery racks appeared in good condition with no notable deficiencies. | none | 2023-04-13 | UPS and it's associated transfer switch were inspected and operated without issue. |  | 2024-10-01 | UPS and it's associated transfer switch were inspected and operated without issue. | None | 2024-10-01 | UPS and it's associated transfer switch were inspected and operated without issue. | None

## Mechanical
Procedure Description |  | Frequency | [8 empty] | Recommended (Rec.) or Required (Req.) | Tunnel Closure Required? | Responsible Party |  |  | Facilities Contract | Comments | Fall 2020 Inpsection |  |  | Fall 2021 Inpsection |  |  | spring 2022 Inpsection |  |  | Fall 2022 Inpsection |  |  | spring 2023 Inpsection |  |  | fall 2023 Inpsection
|  | Weekly | Monthly | Bi-Monthly | Quarterly | Semi-Annually | Annually | Bi-Annually | Tri-Annually | Quinquennial |  |  | ODOT | Consultant | 3rd Party (Mechanic, Electrician, etc.) |  |  | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance
2.1 TVS Axial Fans
Axial Fans
1 | Operate fans and motor-operated dampers and listen for unusual noises |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Fans to be operated Monthly, but on-site inspection as described here should only occur Quarterly. Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No unusual noises noted during operations. | None. | 2022-04-13 | no unusual noises detected |  | 2022-10-01 | No unusual noises noted during operations. | none |  |  |  | 2024-10-01 | No unusual noises noted during operations. | none
2 | Check for undue vibration. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | If present, stop the fan at the earliest opportunity, check impeller for any dirt build-up on the blades, and clean as necessary. Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No undue vibration noted during operations. | None. | 2022-04-13 | no undue vibration detected |  | 2022-10-01 | No undue vibration noted during operations. The SCADA system reported a high vibration on fan TV-01 during the first instance of testing at high speed. The error did not repeat during the next fan test. | none |  |  |  | 2024-10-01 | No undue vibration noted during operations. The SCADA system reported a high vibration on fan TV-01 during the first instance of testing at high speed. The error did not repeat during the next fan test. | none
3 | Operate fans and motor-operated dampers in all configurations. | [5 empty] | X |  |  |  | Rec. | N |  | C | Mech. | Yes | A full SCADA check should be performed. |  |  |  | 2021-09-11 | During the inspection, WSP staff attempted to run the tunnel ventilation system through all emergency ventilation modes via the main tunnel SCADA terminal located in the Lytle tunnel ventilation building. WSP observed during testing that the system did not operate when any of the emergency ventilation modes were initiated at the SCADA terminal. Following this test through the SCADA terminal, WSP attempted initial the emergency ventilation operation by triggering a linear heat detection alarm at the Facility Fire Alarm Control Panel (FACP). This test also failed to initial operation of the emergency ventilation system. It should be noted that all alarms were seen correctly at the tunnel FACP but were not seen at the tunnel SCADA terminal. WSP does not believe this to be a ventilation equipment issue, as all fans and dampers were able to be operated manually at their respective local controllers, in all speeds; and is a SCADA issue. | The Lytle tunnel ventilation system is not operating in any normal or emergency operating modes. This is due to malfunctioning of the ventilation system controls and the tunnel SCADA system. WSP believes that repair / reprogramming / debugging of the ventilation system controls/SCADA system is required to bring the tunnel ventilation system back into working order. | 2022-04-13 | ran fans in hand. | never been able to successfully run through SCADA | 2022-10-01 | The SCADA system operated all fans as intended in all modes. Fan#2 damper #4 is missing the actuator, wires are hanging. Actuator was burning out, so it was removed. However, without the damper actuator the Emergency Fan Modes will not run past the first Fan #1. This damper actuator had to be jumped out in the SCADA program, for the Emergency Fan Modes to run sequential Fan#1, Fan #2, Fan #3. Otherwise, Fan #2 will not start and then Fan #3 will not start. Fan #3 feedback relay to PLC is sticking. Fan #3 reads "off" when Fan #3 steps from LO to HIGH, while apm-meter still reads "running". | Furnish, replace, re-install and re-test fan #2 , damper #4 actuator; Furnsih, replace, re-install and re-test fan #3 feedback relat to PLC | 4.21.2023 | ok |  | 2024-10-01 | ok
4 | Fans should be inspected to ensure that there is no build-up of dirt or other matter that would cause overheating of the motor or obstruct the impeller track. | [5 empty] | X |  |  |  | Rec. | N |  | C |  | No | Cleaning can be done with air or, preferably with a soft brush and vacuum. All connections and fastenings – bolts, clamps etc should be checked to ensure nothing is loose. |  |  |  | 2021-09-11 | No build-up of dirt or debris noted. | None. |  |  |  | 2022-10-01 | No build up of dirt or debris noted. | none |  |  |  | 2024-10-01 | ok
5 | Check all bolts for tightness. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | The bolts to be checked include, canvas connector, fan housing split, duct transition split, duct transition to actuator, fan vibration isolators. Also included are checking the locking collar bolts between the rotor hub and the shaft: verify to a torque rating of 105 lbs. Impeller blades hub cap bolts: verify to a torque rating of 220 ft-lb. Decoder that is attached to the shaft with a locking collar should be verified to be between 25 and 35 in-lbs torque. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
6 | Inspect inside and outside of housing and impeller for wear, deterioration, or build-up of material. | [5 empty] | X |  |  |  | Rec. | N |  | C |  | No |  |  |  |  | 2021-09-11 | Minor surface corrosion on impeller hardware observed | None. |  |  |  | 2022-10-01 | Minor surface corrosion on impeller hardware observed. | none
7 | Verify damper interlocks and operates properly through all positions. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 did not open when activated. | Inspect damper 4 and actuator on TV-2; determine the root cause of failure. Replace necessary parts. | 2022-04-13 | open and close through SCADA |  | 2022-10-01 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 was missing its actuator and could not operate when activated. | Replace actuator
8 | The locking collar between the rotor hub and the shaft has locking screws that should be veriﬁed to a torque rating of 105 ft/lb. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
9 | The impeller blades are held in place to the hub by cap bolts that should be veriﬁed to a torque rating of 220 ft/lb. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
10 | The decoder is attached to the shaft with a locking collar that should be veriﬁed to be between 25-35 inches/lb. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
11 | Inspect ventilation opening grating in Lytle Park for deterioration or condition issues | [7 empty] | X |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
12 | Check air flow measurements in each of the tunnels. | [7 empty] | X |  | Rec. | Y |  | C |  | No |  |  |  |  | 2021-09-11 | Air flow in tunnel bores sufficient. | None. |  |  |  | 2022-10-01 | Air flow in tunnel bores sufficient. | none
Fan Motor
13 | Check and record bearing and winding temperatures. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | If elevated temperature readings are found, investigate equipment condition and/or lubricant condition and level. Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | Temperatures normal, no elevated temperatures noted. | None. | 2022-04-13 | refer to DK report |  | 2022-10-01 | Temperatures normal, no elevated temperatures noted. | none
14 | Clean up of fan motor. | [5 empty] | X |  |  |  | Rec. | N |  | C |  | No | Clear away the dust and dirt on outside surface of enclosure and measure. insulation resistance. |  |  |  | 2021-09-11 | Grease leakage from the back motor bearing on TV-1 and Tv-3 was observed. | Monitor grease leakage. |  |  |  | 2022-10-01 | Grease leakage from the back motor bearing on TV-1, TV-2 and TV-3 was observed | Monitor grease leakage
15 | Check connecting terminals. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Check the connecting bolts (nuts) in terminal box to see whether connecting bolts (nuts) are loose or not. Replace them when necessary. Check the connecting terminals in the terminal box. The connecting terminals in the terminal box should not only be checked for correct tightness but a thermal scan can be taken and printed to verify all crimped terminal ends are correct. The thermal scan will be performed at the end of the day following run testing. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
16 | Check the bolts (nuts). | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Check earthing bolts (nuts), fastening bolts on end shield and internal and external bearing covers, connection of ground lead and setting. External bearing cover bolts can be checked on the external and (decoder end), internal (fan shaft end) are obstructed by the fan hub and axial blades (2,000 lbs.) cannot be easily checked. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
17 | Check bearing. | [6 empty] | X |  |  | Rec. | N |  |  | Mech. | No | Dismounting bearing cap, check whether the grease in bearings has been dirty and dried up or not. It should be replenished as required if there is short of grease. Replace the bearings when necessary. High temperature grease must be adopted according to the motor data sheet. The motor bearing cap is attached to the motor casing. The internal (fan shaft end) is obstructed by the fan hub and axial blades (2,000 lbs.) and cannot be easily removed. The external (RPM decoder end) is less difficult but the bearing is pressed into the motor end housing and very little can be accomplished by just inspecting the outer surface. We suggest that the grease be renewed biannually by removal of the bearing relief plug on the bottom of the bearing housing on the motor. Then ﬂush new grease through the bearing until fresh grease is witnessed at the relief port in the capture vessel. This will be performed at a bi-annual frequency. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
18 | Check the appearance of motors to see whether it has been damaged. Clear away dust and dirt and repair damaged sections. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Yearly maintenance or overhaul consists of quarterly maintenance or routine repair. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
19 | Check windings. | [5 empty] | X |  |  |  | Rec. | N |  |  | Elec. | No | a) Measure insulation resistance on all live parts with a megger and the insulation resistance value should be larger than 1MΩ. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
20 | Bearing purge and grease renewed. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | a) High temperature grease must be adopted according to the motor data sheet. b) The motors are supplied with loose leads. Where a terminal box is fitted, all cable terminations should be tightly secured. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
21 | Motor internal space heater: The amp draw should be veriﬁed on the 110V circuit. Record and review record for consistency. | [6 empty] | X |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
22 | Vibration transmitters on fans: test and record amplitude. Review records for consistency and any aberrations. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
2.2 Isolation Dampers
Fan Isolation Dampers
1 | Operate motor-operated dampers and listen for unusual noises and vibrations |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Perform operational checkout (including cycle testing – opening and closing the damper a few times under electrical power) and verify position status with the main control panel – This can be waived if dampers are cycled on a daily basis during normal use. Qualified ODOT or consultant staff may perform this function. Mechanical contractor to adjust as required. |  |  |  | 2021-09-11 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 did not open when activated. | Inspect damper 4 and actuator on TV-2; determine the root cause of failure. Replace necessary parts | 2022-04-13 | no unusual noises detected |  | 2022-10-01 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 was missing its actuator and could not operate when activated. | Replace actuator |  |  |  | 2024-10-01 | ok
2 | Check bearings for wear and dampers for debris. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Visual inspection only. Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | light debris from fans run cycles. |  | 2022-10-01 | no deficiencies noted | none |  |  |  | 2024-10-01 | no deficiencies noted
3 | Clean damper blades and linkages. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Clean dirt and debris from the damper and actuators. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
4 | Visually inspect dampers and actuators for the build up of dirt, debris, wear and corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | Yes | In general, the dampers must be kept clean and free from foreign matter that may impede normal movement and/or seating of the blades and seals. Therefore, dampers should be cleaned and inspected for general physical and mechanical condition. This inspection should include checking the mechanical tightness of bolted connections, visual inspection for the buildup of dirt or debris that may prevent damper closure and a general inspection for any obvious maintenance. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | light debris from fans cycles. |  | 2022-10-01 | No deficiencies noted | none |  |  |  | 2024-10-01 | ok
5 | Inspect jamb and blade seals for damage and proper sealing. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | Yes |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | blades ok, blade seal showing discoloration |  | 2022-10-01 | No deficiencies noted | none |  |  |  | 2024-10-01 | ok
6 | Inspect the dampers for premature corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | Yes |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | southbound "pit" has water pooling from concrete leak |  | 2022-10-01 | No deficiencies noted | none |  |  |  | 2024-10-01 | ok
7 | Check tightness of mechanical connections |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | Manually check all the fasteners to ensure they are still tight. This can be done by checking with hands only. Generally if a fastener is loose, this will be a noticable check. Tighten all fasteners as necessary. | [6 empty] | 2022-04-13 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
8 | Test internal actuator heater | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Each actuator has an internal heater supplied by a separate 110 volt circuit. These will be tested and amp draw recorded annually to assure proper operation. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
Southbound Tunnel Dampers
9 | Operate motor-operated dampers and listen for unusual noises and vibrations. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Perform operational checkout (including cycle testing – opening and closing the damper a few times under electrical power) and verify position status with the main control panel – This can be waived if dampers are cycled on a daily basis during normal use. Qualified ODOT or consultant staff may perform this function. Mechanical contractor to adjust as needed. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 |  |  | 2022-10-01 | No unusual noises noted during operations | none |  |  |  | 2024-10-01 | ok
10 | Check bearings for wear and dampers for debris. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 |  |  | 2022-10-01 | No deficiences noted. | none |  |  |  | 2024-10-01 | ok
11 | Clean damper blades and linkages. | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Clean dirt and debris from the damper and actuators. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
12 | Visually Inspect dampers and actuators for the build up of dirt, debris, wear and corrosion |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | Yes | In general, the dampers must be kept clean and free from foreign matter that may impede normal movement and/or seating of the blades and seals. Therefore, dampers should be cleaned and inspected for general physical and mechanical condition. This inspection should include checking the mechanical tightness of bolted connections, visual inspection for the buildup of dirt or debris that may prevent damper closure and a general inspection for any obvious maintenance. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 |  |  | 2022-10-01 | The blades on all dampers were covered with some dirt/dust. The feet supporting all damper sections show signs of severe corrosison on the plenum side of the dampers and on the tunnel side of dampers. | none |  |  |  | 2024-10-01 | ok
13 | Inspect jamb and blade seals for damage and proper sealing. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | Yes |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 |  |  | 2022-10-01 | No deficiencies noted. | none |  |  |  | 2024-10-01 | ok
14 | Inspect the dampers for premature corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | Yes |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | "pit" has water pooling from water leak.Fix water leak |  | 2022-10-01 | No deficiencies noted. Isolated instances of corrosion visible on hardware. | None |  |  |  | 2024-10-01 | ok
15 | Check tightness of mechanical connections |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | Manually check all the fasteners to ensure they are still tight. This can be done by checking with hands only. Generally if a fastener is loose, this will be a noticable check. Tighten all fasteners as necessary. | [6 empty] | 2022-04-13 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
16 | Test internal actuator heater | [5 empty] | X |  |  |  | Rec. | N |  |  | Mech. | No | Each actuator has an internal heater supplied by a separate 110 volt circuit. These will be tested and amp draw recorded annually to assure proper operation. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
Coffin Dampers (Damper Doors)
17 | Operate motor-operated dampers and listen for unusual noises and vibrations. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Perform operational checkout (including cycle testing – opening and closing the damper a few times under electrical power) and verify position status with the main control panel. Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No unusual noises noted during operations. | None. | 2022-04-13 | no unusual noises or vibration detected. |  | 2022-10-01 | No unusual noises during operations; A faint "clicking" sound different that the chain noies was observed while closing Northbound coffin damper. | none |  |  |  | 2024-10-01 | ok
18 | Grease bearings using a lithium or lithium complex grease for bearing lubrication. | [5 empty] | X |  |  |  | Rec. | N | O | C |  | No | Qualified ODOT or consultant staff may perform this function. Flush grease annually and replace. | [9 empty] | 2022-10-01 | Not in our scope of work. |  |  |  |  | 2024-10-01 | Not in our scope of work.
19 | Chains are to be lubricated with SAE 10W 40 oil. |  |  |  | X |  |  | X |  |  | Rec. | N | O |  | Mech. | Yes | Qualified ODOT or consultant staff may perform this function. Check lubrication quarterly - regrease bi-annually. | [6 empty] | 2022-04-13 | chains lubricated, good condition |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
20 | Visually inspect diversion walls and blades within opening of 3rd street tunnel. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | ok |  | 2022-10-01 | No deficiencies noted | none |  |  |  | 2024-10-01 | ok
21 | Strength testing of steel blades in the 3rd street ramp ventilation opening. | [7 empty] | X |  | Rec. | Y |  |  | Mech. | No | Qualified ODOT or consultant staff may perform this function. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
22 | Check actuator performance. |  |  |  | X | [5 empty] | Rec. | N | O | C |  | Yes | Covers should not be removed during routine maintenance. Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-04-13 | northbound actuator was leaking and addressed and resealed. |  | 2022-10-01 | Northbound actuator on left side is missing jacketing,. Grease leak observed below right side actuator. | Replace actuator jacketing . Monitor grease leakage. |  |  |  | 2024-10-01 | ok
23 | Actuator battery replacement. | [7 empty] | X |  | Rec. | N |  |  | Mech. | No | Refer to ROTORK maintenance manual for procedures. Initial replacement to occur in Spring 2018 as existing life of battery is unknown. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
2.3 Carbon Monoxide Detection System
1 | Visual inpection |  |  |  | X | [5 empty] | Rec. | Y | O | C |  | Yes | Qualified ODOT or consultant staff may perform this function. |  |  |  | 2021-09-11 | The two north bore air quality monitors were found to have an error message displayed. The air quality monitors in the south bore and south ramp, appeared to be working properly and displayed 0ppm. | The error on the two north bore monitors should be investigated and cleared by a qualified technician. Repairs should be made if determined necessary by the technician. | 2022-04-21 | ok, CO debris starting to build up |  | 2022-10-01 | the Air Quality moitors were operating, however, they were displaying an error message. | The error message indicates the sensors need to be calibrated. A qualified technician should calibrate the sensors and clear the error codes. |  |  |  | 2024-10-01 | ok
2 | Zero Calibration. |  |  |  |  | X |  |  |  |  | Rec. | Y |  |  | Mech. | No | Calibration and maintenance is carried out using a Magnetic Wand, this allows a single user to undertake routine maintenance without needing to access internal components. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
3 | Span Calibration |  |  |  |  | X |  |  |  |  | Rec. | Y |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
4 | Check signal read by PLC/SCADA. |  |  |  |  | X |  |  |  |  | Rec. | Y |  | C |  | Yes | Ensure signal read by the SCADA is same as displayed by the CO detectors at each transmitter. |  |  |  | 2021-09-11 | Readings showed up accurately at the tunnel SCADA terminal. | None. | 2022-04-21 | recorded video in tunnel and in SCADA simultaneously |  | 2022-10-01 | Readings showed up accurately at the tunnel SCADA terminal. | none |  |  |  | 2024-10-01 | Readings showed up accurately at the tunnel SCADA terminal.
2.4 Standpipe
1 | Fire Department Connections Capped and Clear |  |  |  |  | X |  |  |  |  | Req. | N |  | C |  | No | NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems outlines the maintenance criteria and testing procedures for a manual dry standpipe. |  |  |  | 2021-09-11 | FDC capped and clear during inspection. | None. |  |  |  | 2022-10-01 | FDC capped and clear during inspection | none |  |  |  | 2024-10-01 | ok
2 | Confirm threads are undamaged and caps in place. |  |  |  |  | X |  |  |  |  | Req. | Y |  | C |  | No |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. |  |  |  | 2022-10-01 | No deficiencies noted. | none |  |  |  | 2024-10-01 | ok
3 | Confirm top nut and caps are tight but not over-torqued. |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
4 | Operate all control valves by closing and opening low point drains |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
5 | Drain all low point drains. |  |  |  |  | X |  |  |  |  | Req. | Y |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
6 | Inspect piping, hose connections and couplings. | [5 empty] | X |  |  |  | Req. | Y |  | C |  | No |  |  |  |  | 2021-09-11 | During the inspection the standpipe system underwent a hydrostatic test per NFPA 25. The system held pressure at 200psi for 2hrs. The most common standpipe defects observed are listed below. - Corrosion on Fire Hose Valve (FHV) wheel - Missing FHV caps - Unattached FHV cap chains - Corrosion on pipe threads at FHV - Corrosion on 2.5” galvanized branch pipe to FHV - Significant corrosion on standpipe risers, including widespread surface rust and pitting on piping, valves, pipe hangers and couplings. - Pipe labels not long affixed to riser pipes. | 1. Replace all standpipe pipe labels 2. Replace all fire hose valve wheels 3. Replace missing fire hose valve caps 4. Reattach all fire hose valve cap chains |  |  |  | 2022-10-01 | During the inspection the standpipe system underwent a hydrostatic test per NFPA 25. The system passed the test according to the AHJ but lost more than 5 psi as allowed by NFPA test guidelines. The most common standpipe defects observed are listed below. 1.) Corrosion on fire hose valve (FHV) wheel 2.) Corrosion on pipe threads at FHV 3.) Corrosion on 2.5" galvanized branch pipe to FHV 4.) Significant corrosion on standpipe risers, including widespread surface rust and pitting on piping, valves, pipe hangers and couplings. | Replace all fire hose valve wheels |  |  |  | 2024-10-01 | ok
7 | Test flow hydrant. |  |  |  |  | X |  |  |  |  | Req. | N |  |  | Other | No | This element is the responsibility of the City. | [15 empty] | 2024-10-01 | ok
8 | Hydrostatic testing of the system. | [8 empty] | X | Req. | Y |  |  | Mech. | No | Cincinnati Fire Department should be invited to witness this test. | [9 empty] | 2022-10-01 | system passed | 4 accessible valves in the tunnels and 1 valve under sidewalk along 4th street to be replaced. | 2023-03-01 | ok |  | 2024-10-01 | ok
2.5 Soundproofing
Fan Sound Attenuation
1 | Visually inspect fan sound attenators for the build up of dirt, debris, wear and corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | No |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. |  |  |  | 2022-10-01 | No deficiencies noted | none |  |  |  | 2024-10-01 | ok
Soundproofing Boards
2 | Visually inspect fan soundproofing boards for the build up of dirt, debris, wear and corrosion. |  |  |  |  | X |  |  |  |  | Rec. | N |  | C |  | No |  |  |  |  | 2021-09-11 | No deficiencies noted. | None. |  |  |  | 2022-10-01 | No deficiencies noted. | none |  |  |  | 2024-10-01 | ok
2.6 HVAC
Commercial Electric Unit Heater
1 | Check the tightness of all visible bolts and nuts, in particular the support structure bolts and nuts. Similarly check the motor mounting bolts located in the top and back of the heater case. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | Potentially lethal voltages are present. Be sure to lock the branch circuit disconnect switch in the OFF position and tag the circuit “Out for Maintenance” before working on this equipment. | [6 empty] | 2022-04-18 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
2 | Check the motor, fan, discharge openings, intake openings, heating elements and control compartment for cleanliness. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | If necessary, clean by using a vacuum or compressed air. Be careful not to bend the fan blade propeller. | [6 empty] | 2022-04-18 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
3 | Check that the electric motors are permanently lubricated and thermally protected. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
4 | Inspect all terminal connections, contactor and conductor insulation for damage, looseness, fraying, etc., as applicable. Tighten any loose terminals and replace or repair wire with damaged or deteriorated insulation. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | Badly pitted, welded together, or burned shall be replaced. | [6 empty] | 2022-04-18 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
Fans
5 | All fasteners should be checked for tightness each time maintenance checks are performed prior to restarting unit. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
6 | Motor maintenance is generally limited to cleaning and lubrication (where applicable). |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | ok |  | 2022-10-01 | The tunnel ventialtion fans were all found to be in good condition exhibiting no significant signs of corrosion or deterioration. All fans displayed signs of minor grease leakage similar to what is shown on TV-1 Fans. |  | 4.21.2023 | ok |  | 2024-10-01 | ok
7 | Motors supplied with grease fittings should be greased in accordance with manufacturer’s recommendations. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | Where motor temperatures do not exceed 104°F (40°C), the grease should be replaced after 2000 hours of running time as a general rule. All bearings on standard Model BSQ fans are factory lubricated and require no further lubrication under normal use (between -20°F and 180°F in a relatively clean environment). | [6 empty] | 2022-04-18 | no grease per note |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
8 | Belts should be checked periodically for wear and tightness. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | For belt replacement, loosen the tensioning device far enough to allow removal of the belt by hand. Do not force belts on or off. This may cause cords to break, leading to premature belt failure. Once installed, adjust belts as shown in “Pre-Starting Checks.” Replace belts every 2 years. | [6 empty] | 2022-04-18 | belt in good condition. |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
Dampers
9 | Operate motor-operated dampers and listen for unusual noises and vibrations |  |  |  | X | [5 empty] | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | no unusual noises or vibration detected. |  | 2022-10-01 | The dampers were found to be in good condition only exhibiting areas of superficial corrosion or deterioration. Fan damper 4 on TV-2 was missing an actuator and could not be operated. |  | 4.21.2023 | SCADA had damper open in override; has been reset in auto; Repair made to end switch was not recording correctly |  | 2024-10-01 | ok
10 | Check bearings for wear and dampers for debris. |  |  |  | X | [5 empty] | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | ok |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
11 | Visually inspect dampers and actuators for the build up of dirt, debris, wear and corrosion. |  |  |  | X | [5 empty] | Rec. | N |  |  | Mech. | Yes | a) If cleaning is necessary, use mild detergents or solvents. Clean with a non-oil based solvent. b) If lubrication is desired for components such as axle bearings, jackshaft bearings and jamb seals, do not use oil-based lubricants or any other lubricants that attract contaminants such as dust. | [6 empty] | 2022-04-18 | new stickers added. |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
12 | Test smoke dampers. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | They will be cycle tested by voltage drop to assure proper function. They will not be tested through the ﬁre alarm system. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
Split-System
13 | Check vertical centrifugal pump. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | Ensure pump is automatically starting and stopping and performing as designed. | [12 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
14 | Pull outdoor unit access door and clean bottom of the unit of dirt or debris. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
15 | Check outdoor coil for cleanliness and clean if needed |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
16 | Check indoor filters, clean and/or change as needed |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
17 | Inspect indoor coil and indoor blower for cleanliness |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
18 | Tighten all electrical connections |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
19 | Check condenser fan blades for tightness |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
20 | Inspect contactor contacts |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
21 | Check and record temperature drop across evaporator coil |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
22 | Inspect overall operation of unit |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | S.S. in good condition, light debris on filters which were cleaned. Batteries also |  |  |  |  | 4.21.2023 | ok |  | 2024-10-01 | ok
23 | Visual inspection for refrigerant leaks |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
24 | Check “error history" and execute delete error history |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
25 | Select “self check" and confirm no errors existing |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
26 | Execute "test run" and inspect outdoor unit for proper operation |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | [13 empty] | 4.21.2023 | ok |  | 2024-10-01 | ok
27 | Make recommendations of any required repairs |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | Yes | [7 empty] | 2022-04-18 | no recommendations at this time. |  |  |  |  | 4.21.2023 | no recommendations at this time |  | 2024-10-01 | ok
28 | Carry out a malfunction-diagnosis using the remote controller. |  |  |  |  | X |  |  |  |  | Rec. | N |  |  | Mech. | No | When a malfunction occurs to air conditioner, both indoor unit and outdoor unit will stop and operation lamp blinks to inform unusual stop.

## Structural
Procedure Description |  | Frequency | [8 empty] | Recommended (Rec.) or Required (Req.) | Tunnel Closure Required? | Responsible Party |  |  | Comments | Fall 2020 Inpsection |  |  | Fall 2021 Inpsection |  |  | Fall 2022 Inpsection |  |  | Fall 2023 Inpsection
|  | Weekly | Monthly | Bi-Monthly | Quarterly | Semi-Annually | Annually | Bi-Annually | Tri-Annually | Quinquennial |  |  | ODOT | Consultant | 3rd Party (Mechanic, Electrician, etc.) |  | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance | Date Completed | Inpsection Comments / Notes | Recommended Repairs / Maintenance
Portals
1 | Stone/Veneer Facing Inspection | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect for cracked, separated/leaning veneer, etc on portals and wingwalls with each structural inspection. |  |  |  | 2021-09-11 | Isolated locations of masonry veneer cracked or spalled and isolated locations of mortar failure between the edges of the masonry veneer and the concrete portal with up 1/4" wide gaps between mortar and concrete. Retaining wingwalls with isolated missing stones on masonry veneer. Fourth panel from north portal on Wall 11, masonry veneer leaning up to 4" on north side. Saddle catch plates installed. | Monitor leaning masonry veneer. | 2022-10-02 | Isolated locations of masonry veneer cracked or spalled and isolated locations of mortar failure between the edges of the masonry veneer and the concrete portal with up 1/4" wide gaps between mortar and concrete. Retaining wingwalls with isolated missing stones on masonry veneer. Fourth panel from north portal on Wall 11, masonry veneer leaning up to 4" on north side. Saddle catch plates installed. | Monitor leaning masonry veneer. | 2024-10-01 | Isolated locations of masonry veneer cracked or spalled and isolated locations of mortar failure between the edges of the masonry veneer and the concrete portal with up 1/4" wide gaps between mortar and concrete. Retaining wingwalls with isolated missing stones on masonry veneer. Fourth panel from north portal on Wall 11, masonry veneer leaning up to 4" on north side. Saddle catch plates installed. | Monitor leaning masonry veneer.
2 | Lintel- Concrete area directly over portal. | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect for cracks, spalls, loose concrete over traffic. Remove any loose concrete areas over traffic or near traffic during inspection. |  |  |  | 2021-09-11 | Multiple areas of fiberwrapped patches. On North Portal over right edge line of Nourthbound Mainline roadway, linear heat detection wire support not reinstalled after fiberwrap installation. Wire sagging into vehicular envelope. | Reinstall linear heat detection wire support. | 2022-10-02 | Multiple areas of fiberwrapped patches | none | 2024-10-01 | Multiple areas of fiberwrapped patches | none
3 | Fence | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Inspect for loose connections, deterioration, sturdiness, etc. |  |  |  | 2021-09-11 | No deficiencies noted. | None. | 2022-10-02 | No deficiencies noted | none | 2024-10-01 | No deficiencies noted | none
4 | Capstone | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect for cracks, spalls, loose concrete over traffic. Remove any loose concrete areas over traffic or near traffic during inspection. |  |  |  | 2021-09-11 | South Portal over centerline of Southbound Mainline roadway, 9-1/2" wide delaminated area 6" tall on vertical face and extending 10" onto top horizontal face. | Patch delaminated area on South Portal over Southbound Mainline roadway. | 2022-10-02 | South portal over centerline of southbound mainline roadway, 9.5 inch wide delaminated area 6" tall on vertical face and extending 10 inch onto top horizontal face. | Patch delmaninated area on south portal over southbound mainline roadway. | 2024-10-01 | Minor deficiencies noted | none
Within Vehicular Tunnels
1 | Tiles |  |  |  |  | X |  |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect all tiles visually. Using a rubber mallet, Sound tiles near all cracks, joints, or other missing tiles. Remove all unsound tiles with a steel headed hammer and/chisel. Consultant to do this during the one structural inspection. ODOT to do this all other occasions. |  |  |  | 2021-09-11 | Areas of unsound tiles removed throughout all three tunnel roadways, specifically at expansion joint locations. Delaminated, cracked, or missing tiles are common along joint headers and at isolated locations between joints. | Monitor tiles adjacent to missing tile locations. | 2022-10-02 | Areas of unsound tiles removed throughout all three tunnel roadways, specifically at expansion joint locations. Delaminated, cracked , or missing tiles are common along joint headers and at isolated locations between joints. | Monitor tiles adjacent to missing tile locatons. | 2024-10-01 | Areas of unsound tiles removed throughout all three tunnel roadways, specifically at expansion joint locations. Delaminated, cracked , or missing tiles are common along joint headers and at isolated locations between joints. | Monitor tiles adjacent to missing tile locatons.
2 | Fireproofing | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect fireproofing (white, untiled areas of wall walls). Sound all areas with cracks. Randommly sound other areas. Only remove if displacement is showing or at the direction of the ODOT Project Manager |  |  |  | 2021-09-11 | Heavy hairline map cracking spaced at 3" to 6" on roof and at 6" to 12" on walls. Isolated locations of delaminated and spalled fireproofing with exposed wire mesh reinforcing. | Monitor firerproofing deterioration. | 2022-10-02 | Heavy hairline map cracking spaced at 3" to 6" on roof and at 6" to 12" on walls. Isolated locations of delaminated and spalled fireproofing with exposed wire mesh reinforcing. | Monitor fireproofing deterioration. | 2024-10-01 | Heavy hairline map cracking spaced at 3" to 6" on roof and at 6" to 12" on walls. Isolated locations of delaminated and spalled fireproofing with exposed wire mesh reinforcing. | Monitor fireproofing deterioration.
3 | Barrier | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Inspect for accident damage, spalls, snag points, etc. |  |  |  | 2021-09-11 | Full height hairline cracks spaced at 4'. 54" long by 4" wide by 1/4" deep gouge from impact on east barrer in Northbound Mainline roadway at Station 127+60. Isolated collision scrapes and gouges throughout all barriers. Reflectors mounted to the parapets typically broken or missing. | None. | 2022-10-02 | Full height hairline cracks spaced at 4 foot .54 inch long by 4 inch wide by 1/4 inch deep gouge from impact on east barrier in northbound mainline roadway at station 127+60. Isolated collision scrapes and gouges througout all barriers. Reflectors mounted to the parapets typically broken or missing. | none | 2024-10-01 | Full height hairline cracks spaced at 4'. 54" long by 4" wide by 1/4" deep gouge from impact on east barrer in Northbound Mainline roadway at Station 127+60. Isolated collision scrapes and gouges throughout all barriers. Reflectors mounted to the parapets typically broken or missing. | none
4 | Wearing Surface | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Visually inspect for cracking, spalling, etc. Notify maintenance staff immediately of any potholes that need patched. |  |  |  | 2021-09-11 | Full width transverse cracks up to 1-1/2" (1/4" typical) at tunnel section expansion joint locations. Isolated gouges up to 3/4" deep. | None. | 2022-10-02 | Full width transverse cracks up to 1.5 inch (1/4 inch typical) at tunnel section expansion joint locations. Vertical displacement up to 5/8 inch noted at joint locations. | Monitor crack sealer in roof joints. | 2024-10-01 | Full width transverse cracks up to 1.5 inch (1/4 inch typical) at tunnel section expansion joint locations. Vertical displacement up to 5/8 inch noted at joint locations. | Monitor crack at wearing surface joints
5 | Joints | [5 empty] | X |  |  |  | Req. | Y | Even Year | Odd Year |  | Inspect joints for signs of recent moisture (wetness, staining, etc.), separation or displacement. |  |  |  | 2021-09-11 | Crack sealer in roof joints at expansion joint locations beginning to crack and is missing at isolated locations. Vertical displacement up to 5/8" noted at joint locations. | Monitor crack sealer in roof joints. | 2022-10-02 | The tunnel liners and interior walls exhibit hairline cracks in the tiles and isolated spalls with exposed reinforcing and delaminated areas, typically adjacent to construction and expansion joint locations. Full height vertical cracks up to 1/16 inch wide were noted in the interior walls between the southbound ramp and southbound mainline (wedge room area). | Epoxy inject cracks, patch spalled areas, and montor areas of water leakage. | 2024-10-01 | The tunnel liners and interior walls exhibit hairline cracks in the tiles and isolated spalls with exposed reinforcing and delaminated areas, typically adjacent to construction and expansion joint locations. Full height vertical cracks up to 1/16 inch wide were noted in the interior walls between the southbound ramp and southbound mainline (wedge room area). | Monitor crack sealer in roof joints.
6 | Overall Structure | [5 empty] | X |  |  |  | Req. | N | Even Year | Odd Year |  | Much of the structural componenents/concrete are covered by tile, veneer, etc. Inspection overall structure for signs of structural distress or deterioration such as displacmeent, contigious cracking, settlement, spalling, moisture, sinkholes, etc. |  |  |  | 2021-09-11 | The tunnel liners and interior walls exhibit hairline cracks in the tiles and isolated spalls with exposed reinforcing and delaminated areas, typically adjacent to construction and expansion joint locations. Full height vertical cracks up to 1/16" wide were noted in the interior walls between the Southbound Ramp and Southbound Mainline (wedge room area). | Epoxy inject cracks, patch spalled areas, and monitor areas of water leakage. | 2022-10-02 | Abandon lane reminder light locations checked for connection | none | 2024-10-01 | The tunnel liners and interior walls exhibit hairline cracks in the tiles and isolated spalls with exposed reinforcing and delaminated areas, typically adjacent to construction and expansion joint locations. Full height vertical cracks up to 1/16" wide were noted in the interior walls between the Southbound Ramp and Southbound Mainline (wedge room area). | Monitor crack tiles and tiles adjacent to missing tile locations.
Mechanical / Electrical /Fan / Plenum areas | [19 empty] | 2021-09-11 | Linear heat detection wire supports at two locations missing/pulled out. Cracked lense on abandoned lane reminder light removed at one location. Abandoned lane reminder light locations checked for connection. | Reinstall linear heat detection wire supports.
1 | Mechanical / Fan Rooms | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. |  |  |  | 2021-09-11 | Isolated full height hairline cracks in walls. Standing water noted in access room between fan room and mechanical room. | Monitor water. | 2022-10-02 | Isolated full height hairline cracks in walls. Standing water noted in access room between fan room and mechical room. | Monitor water | 2024-10-01 | Isolated full height hairline cracks in walls. Standing water noted in access room between fan room and mechanical room. | Monitor water
2 | Electrical Rooms | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. Check for cracking in area immediately around floor hangers (round columns) over tunnel area. |  |  |  | 2021-09-11 | Isolated full height cracks up to 1/16" wide in walls. Crack gauge installed on wall between plenum space and electrical room. | Monitor cracks. | 2022-10-02 | Isolated full height cracks up to 1/16 inch wide in walls. Crack gauge installed on wall between plenum space and electric room | Monitor cracks. | 2024-10-01 | Isolated full height cracks up to 1/16" wide in walls. Crack gauge installed on wall between plenum space and electrical room. | Monitor cracks.
3 | Plenum Space | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. Check for cracking in area immediately around floor hangers (round columns) over tunnel area. |  |  |  | 2021-09-11 | Isolated full height cracks up to 1/16" wide in walls. Crack gauge installed on wall between plenum space and electrical room. No distress noted in roof slab surrounding hangers. Hanger shell pipes have minor surface corrosion at base. | Monitor cracks. | 2022-10-02 | Isolated full height cracks up to 1/16 inch wide in walls. Crack gauge installed on wall between plenum space and electric room. No distress noted in roof slab surrounding hangers. Hanger shell pipes have minor surface corrosion at base. | Monitor cracks. | 2024-10-01 | Isolated full height cracks up to 1/16" wide in walls. Crack gauge installed on wall between plenum space and electrical room. No distress noted in roof slab surrounding hangers. Hanger shell pipes have minor surface corrosion at base. | Monitor cracks.
4 | Hallways, stairs, passageways. | [5 empty] | X |  |  |  | Rec. | N | Even Year | Odd Year |  | Inspection overall structure for signs of structural distress or deterioration such as cracking, displacmeent, settlement, spalling, moisture, mold, etc. |  |  |  | 2021-09-11 | Full height spall (17" wide by 1" deep) with active leakage in north wall at west end of hallway from main access stairs. Hallway between fan room and plenum space with heavy mold/mildew smell. Standing water in southeast stairway to plenum space along east wall. Isolated full height cracks up to 1/16" wide in walls. | Epoxy inject/patch spall with leakage. Monitor cracks areas of standing water. | 2022-10-02 | Full height spall (17 inch wide by 1 inch deep) with active leakage in north wall at west end of hallway from main access staris has been patched but is cracking and deteriorating. Hallway between fan room and plenum space with heavy mold/mildew smell. Standing water in southeast stairway to plenum space along east wall. Isolated full height cracks up to 1/16 inch wide in walls. | Monitor patched spall, reapply epoxy injection to assist with leakage. Monitor cracks and areas of standing water. | 2024-10-01 | Full height spall in north wall at west end of hallway from main access staris has been patched but is cracking and deteriorating. Standing water in southeast stairway to plenum space along east wall. Isolated full height cracks up to 1/16 inch wide in walls. | Monitor deficiencies

## Inspection-Entry Log
Inspection/Entry Log- record all tunnel inspection events (strucutral/accident/special/mechanical/electrical/Tour/etc.)
Names of Entrants | Date | Purpose | Issues Found | Actions taken | Critical Finding? | If yes, notify FHWA (now Alexis Bogen) and OSE (now Jared Backs) and record communication below. | Immeidate action (Remove loose concrete, etc). | Final Resolution (Repair contract, etc.)
Stephanie Lentz (BS2) and co-ops | 2019-03-15 | Periodic Inspection | Puddles found in several areas of tunnel interior after rain.
Stephanie Lentz (BS2) | 2019-04-16 | Periodic Inspection | Puddles found in several areas of tunnel interior after rain.
Stephanie Lentz (BS2) | 2019-04-25 | Alarm sounded after cleaning | Eventually determined that a failed CO sensor were at fault (moisture). | Sensors were replaced by Glenwood Electric through isnpection contract.
David Krazl (BS2), Consultant Mechanical and Electrical team | 2019-05-13 | Inspect NB Portals during cleaning and consultant Mechanical/Electical inspect. | Loose concrete on capstone and lintels were found as well as a couple loose tiles. | Loose concrete and tiles were removed. | Y | Notified FHWA (Matt Shamis) on 9/17/18. | Loose concrete and tiles removed | Project is scheduled to replace/repair.
David Krazl (BS2), Consultant Mechanical and Electrical team | 2019-05-31 | Inspect SB Portals during cleaning and consultant Mechanical/Electical inspect. | Loose concrete on capstone and lintels were found as well as a couple loose tiles. | Loose concrete and tiles were removed. | Y | Notified FHWA (Matt Shamis) on 9/17/18. | Loose concrete and tiles removed | Project is scheduled to replace/repair.
David Krazl (BS2) | 2019-06-14 | Periodic Inspection | 1 of 6 ventilation hatch doors had a chain "derailed". | Inspector reset chain.
Stephanie Lentz (BS2) | 2019-06-20 | Periodic Inspection- Recheck derailed chain | Puddles found in several areas of tunnel interior after rain. (Chain OK) | No action.
Stephanie Lentz (BS2) | 2019-07-22 | Periodic Inspection- Follow up after maint CO sensor replacement | Bad sensors had been replaced by consultant/maint contract. Puddles. | No action.
Collett (NTIS-ODOT D8), Meyer, Keller (OSE), Brokaw (NTIS OSE), Shamis (FHWA), Tong (FHWA) | 2019-08-13 | 2019 NTIS Compliance meeting with FHWA | 1/4" water build-up in stairway from wall leakage. A couple electrical boxes left open. | No action.
Collett (NTIS-ODOT D8), Ray Kinzer (BS2), Eric Schmidt (BS1), Consultant Mechanical and Electrical Team, Maintenance/cleaning Crew, Marvin Lennon (ODOT Construction) | 2019-09-13 | Annual inspeciton of SB Ramp tunnel interior and portals, cleaning of SB mainline. | Measured section of leaning façade on SB wingwall at approximately 2.25". Removed a few loose tiles at joints. | Removed a few loose tiles at joints. Loose wall façade was temporarily restrained. A project is to be sold in 2020 to pin the façade back to the wall in all locations. | Y | FHWA (Kenny Tong) is aware per 12/23/19 email referencing the Fall 2018 inspection. | Restraint installed. | A project is scheduled to anchor the stone to the façade.
Ray Kinzer (BS2), Dave Krazl (BS2), Consultant Mechanical and Electrical Team, Maintenance/cleaning Crew | 2019-09-14 | Annual inspection of SB mainline interior and protals, cleaning of SB Ramp tunnel | A few loose tiles at joints were found. | They were removed immediately.
Stephanie Lentz (BS2), Ron Kesterson (BS1) | 2019-09-27 | Annual inspection of NB mainline interior and portals | A few loose tiles at joints were found. | They were removed immediately.
Kinzer (BS2) | 2019-10-07 | Investigated complaint of something in tunnel falling and cracking windshield (silver dollar size) | Nothing found except a few small rocks on the shoulder. No broken tiles found on ground. Assume issue was road debris. | Reported finding to Dsitrict Bridge Engineer.
S. Lentz (BS2) | 2019-11-12 | Periodic Inspection | Fan 1 louvers open. | Reported finding to Dsitrict Bridge Engineer.
R Kinzer ( BS2) | 2019-12-17 | Periodic Inspection | Puddles along old walls in interior and Fan 3 louvers open | Reported to District Bridge Engineer
n/a | 2019-12-30 | follow up to Kinzer inspection 12.17.2019 | Puddles formed due to saturated conditions outside leaking through concrete control joint; Fan 3 louver open | Spoke with construction engineer and consultant 12/30/2019; Control joint has been capped, but will be repaired again due to leaks; drain is collecting the water; Open louver fan #3 due to error in SCADA system, maintenance consultant has been made aware of this 1/16/2020 and will work with Outbound and repair | N
Jim Bauer and new TM | 2020-02-06 | Tour of tunnel to new TM | Coffer door on northbound lanes is wide open.
Jim Bauer and Justin Kemp | 2020-03-20 | Fire panel alert | Coffer door on northbound lanes is still wide open. | to be discussed with Hatch Mott tomorrow's conf call; last repsonse from Hatch Mott via email this is normal operation, but check SCADA logs to confirm
S. Lentz (BS2) | 2020-03-31 | Periodic Inspecton | Fan 3, louvers open. Areas of water in Plenum room, in room with large access hatch and small area between fans 2 and 3 in sound proof area. Light fixture over 1st set of louvers along SB 71 not working. | Reported to District Bridge Engineer
Joe Smithson / Alec Sadowski (ODOT Engineering PM / Geotech) | 2020-04-02 | Reboot server for CO IT (Mike Blake). Check NB Coffer door | Rebooterd server with help of Outbound/Glenwood. NB Coffer doors open due to limit switch. Sensors needing replaced were at olded (concreted over) air intake due to leakage. |  | N
R Kinzer & E Schimdt | 2020-08-24 | Periodic Inspection | Water in Plenum space room at doors and grate/drain cleaned out. Was showing error on screen Main SVR main 1 Error # 1914 | Reported to District Bridge Engineer
S. Lentz (BS2) | 2020-11-25 |  | Leakage in Plenum area on south wall, water pumping through and flowing to drain. Water is also coming thru hatch/grate over NB tunnel, north end, passing under door and flowing through control room. Motor on west side of damper over NB 71 has oil leaking, the wheel below this leak which is used to open damper manually is full of oil. Also an area of leakage in room east of electrical room, along east wall. Several fluorescent light fixtures are not working. (Not in the portals.) The computer used to check the status of systems is reporting "No Internet". (Could not get back online.) Photos can be seen at J:\structures\bridges\20 photos\HAM\IR 71\0134\Periodic Inspection 11-25-2020. | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2021-01-22 | Periodic Inspection | Found new areas of leakage, in Units 18, two rooms west of area with control panels. Both appear to be new, I have not seen leakage here previously. The room just south of panel room has leakage along top of wall and room directly west of there has leakage running across floor, from north wall, out of room and down stairway to access door to SB IR71. Water has also reappeared in hallway from entrance to plenum room at last set of stairs and is still leaking inside plenum room. Oil still leaking at motor for NB damper. Found traces of fluid leeking on damper motors for fans, F1-3.4 and F1-1.4. Scada system showing alarms. | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2021-02-26 | Periodic Inspection | Found additional new areas of leakage; previous leakage at bottom of stairs to Plenum Room is now pooling and running into plenum and down walls around dampers and moving into curb/shoulder area of SB 71. The previous leakage in the plenum room has gotten heavier and there is now some dampness coming from the top of the wall close to access door to plenum. The previous leakage running down stairs and wall to access door for SB 71 has gotten heavier and is running under door and into shoulder and lane of SB 71. Photos at J:\structures\bridges\21 photos\HAM\IR 71\0134\Maintenance Contract 2-2021\2-26-2021\PDF. Glenwood was removing existing fluorescent lights and replacing with LED. The fire detectors at the south end of portals are not relaying to system. | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2021-04-15 | Periodic Inspection | Contractor appears to have alleviated several areas of leakage. The previous leakage in stairway to Plenum room has stopped along lower stairs but there is now a smaller leak coming from about center of wall, this is between the stairway from the entrance and the stairs to plenum. Still some dampness in the first damper area to SB IR71. Motor to dampers for NB IR71 is still leaking oil and wheel for manually opening damper is full of oil. The fire alams on the SCADA system were fewer this inspection but the alarm on the south end of portals in still not responding. Fan controls appear to be set in manul mode. Lock out tag to several boxes in Electric Contro Room. Pictures at J:\structures\bridges\21 photos\HAM\IR 71\0134\Periodic Inspection 4-15-2021 | Reported to District Bridge Engineer
S. Lentz (BS2) | 9/16 and 9/20/2021 | Periodic Inspection and to allow Contractors Access to Tunnel | 9/16/2021 Unlocked tunnel to allow contractor from Outbound access, having issues with fan response to SCADA. Dampers on Fan 2 are open. Delamed area in stairway wall, site of previous injections to stop leaks. Unlocked tunnel on 9/20/2021 to allow Northwestern Ohio Security Systems, Inc. to address problems with security camera in Control Room, has not been repaired. The damper over the NB tunnel is open, was not open when tunnel was locked on the 16th. Also have water seeping into room east of electrical room (has access hatch) under doors to ventilation and under fan 1 into fan room. | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2021-09-23 | Periodic Check | Returned to tunnel to close damper in NB tunnel. Switched SCADA System to manual, closed door and reset system to automatic. | Reported to District Bridge Engineer | N
| 2021-10-08 | Periodic Check | Water seeping into room east of electrical room (has access hatch) under doors to ventilation and into fan room under fan 1. Damper over NB tunnel open for 2nd time, switched SCADA to manual mode to close. Motor for damper of NB tunnel still appears to be leaking, wheel below motor has been cleared of previous oil buildup. Photos at J:\structures\bridges\21 photos\HAM\IR 71\0134\10-08-2021. | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2021-10-19 | Periodic Check | Opened tunnel to allow contractor from NWOSS to install new camera in control room. Removed trash and debris from several areas. Motor on damper for NB tunnel appears to have been repaired, cover has not been placed back on motor. Cover was also off motor for the dampers on fan 2, dampers were closed this inspection. Photos at J:\structures\bridges\21 photos\HAM\IR 71\0134\10-19-2021 | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2021-10-29 | Replace Fire Extinguishers | Replaced fire extinguishers in cabinets on west wall of SB portal. Locks on cabinets were rusted beyond repair or use, placed "turn buttons" on frame to keep cabinet doors shut. Replaced extinguishers in passageway and into conrol room, numbers 1, 2 and 3. New canisters will not hang on brackets, canisters are on floor at this time. Photos at J:\structures\bridges\21 photos\HAM\IR 71\0134\1-29-2021 Fire Extiguisher Cabinets and inside Passage Ways. | Reported to District Bridge Engineer | N
E Schmidt (BS1) | 2021-12-10 | Periodic Inspection. Outbound Technologies on site. | Water in Plenum space room. Water ponding at bottom of the stairs in hallway to plenum space room. Placed cover on motor. Checked exit signs emergency lighting. J:\structures\bridges\21 photos\HAM\IR 71\0134\Periodic Inspection 12-10-2021 | Report to District Bridge Engineer
S. Lentz (BS2) | 2022-02-15 | Periodic Inspection | Water in Plenum space room. Water ponding at bottom of the stairs in hallway to plenum space room. Water also ponding along floor behind dampers 1 and 2 for SB 71 portal and at access door to SB portal. Damper was open over SB ramp lane and at fan 2. Closed both. Fire alarms were noted on SCADA. Checked exit signs emergency lighting. J:\structures\bridges\22 photos\HAM\IR 71\0134 | Reported to District Bridge Engineer | N
S. Lentz (BS2) | 2022-03-15 | Periodic Inspection and to allow access for inspection of fire extinguishers. | Water in Plenum space room. Water ponding at bottom of the stairs in hallway to plenum space room. Water also ponding along floor behind dampers 1 and 2 for SB 71 portal and at access door to SB portal. J:\structures\bridges\22 photos\HAM\IR 71\0134\Periodic Inspection 3-14-2022 | Reported to District Bridge Engineer | N
Eric Schmidt and Dwayne Bishop | 3/31/2022 and 4/1/2022 | Performed maintenance items per the spring 2022 Lytle Tunnel Cleaning/maintence | all items have been taken care of per 4.12.2022 email to inspectors from Jeff Meyer and IOC found here. I:\Structures\ham\IR 71\0134\After 2015 Rehab\Inspection & Maint contract\Inspections\2021 Tunnel Inspection\Fall Draft Inspection\comments
Stephanie Lentz and Eric Schmidt | 4/1/2022 and 4/2/2022 | Performed maintenance items per the spring 2022 Lytle Tunnel Cleaning/maintence | all items have been taken care of per 4.12.2022 email to inspectors from Jeff Meyer and IOC found here. I:\Structures\ham\IR 71\0134\After 2015 Rehab\Inspection & Maint contract\Inspections\2021 Tunnel Inspection\Fall Draft Inspection\comments
Jeff Meyer and Corey Owens | 4/2/2022 and 4/3/2022 | Performed maintenance items per the spring 2022 Lytle Tunnel Cleaning/maintence | all items have been taken care of per 4.12.2022 email to inspectors from Jeff Meyer and IOC found here. I:\Structures\ham\IR 71\0134\After 2015 Rehab\Inspection & Maint contract\Inspections\2021 Tunnel Inspection\Fall Draft Inspection\comments
C. Owens (BS1) and S. Lentz | 2022-05-16 | periodic inspection | Water in Plenum space room. Water ponding at bottom of the stairs in hallway to plenum space room. Placed cover on motor for dampner, on SB of plenum. Checked exit signs emergency lighting big dampner for NB was opened and is now closed and the dampner for big fan 2 was open and now closed.\\D08fs100\archives\structures\bridges\22 photos\HAM\IR 71\0134\Periodic Inspection 5-16-2022 | Reported to District Bridge Engineer | n
C. Owens (BS1) | 2022-06-21 | periodic inpection | there was a contractor in last week doing some patching and some repairs. Outside plenum has a little water ponding the big dampner on NB motor seal has been repaired. And big fan #2 has a dampner motor removed and out for repairs. J:\structures\bridges\22 photos\HAM\IR 71\0134\periodic inspection 6-21-2022 |  | N
C. Owens (BS1) | 2022-08-09 | periodic inpection | FI-2.4 dampner motor still missing at this time. Servers are still in the process of being updated and all the bugs worked out. There is still some water on leaking on the east room next to the electrical room.J:\structures\bridges\22 photos\HAM\IR 71\0134\periodic inspection 8-9-2022 | Reported to District Bridge Engineer | n |  |  | email received 9.6.2022 Debra Kuempel failed acutator will take 3 to 4 weeks for re-build; email received 9.7.22 PerkinsCarmack new actuators are no longer manufactured as a back-up
Stephanie Lentz (BS2) | 2022-08-15 | Check Fire Alarm System | Receiving numerous alerts from system. Reset fire alarm system, mentioned issues with battery backup. Photos at J:\structures\bridges\22 photos\HAM\IR 71\0134\Alarm Check 8-15-2022 | Reported to District Bridge Engineer | n
Stepahanie Lentz (BS2) | 2022-08-17 | Issues with Alerts from System. Receiving constant notices from fire alarm system. | Met contractor, Doug from Johnson Controls. Replaced both backup batteries for fire monitoring system, feels this could be the problem causing the constant alerts. Please let them know if issue continues. Photos at J:\structures\bridges\22 photos\HAM\IR 71\0134\Alarm Check, Met Contractor 8-17-2022 | Reported to District Bridge Engineer | n
C. Owens (BS1) | 2022-10-14 | periodic inspection | just had contractors in the couple weeks prior, no alarms and the FI-2.4 actuator motor was finaly fixed and put back. There was a little water in the back room next to the electrical room. Fan 1 looks to have a little bit of oil coming off the rear of the motor. Other than that all looked good at this time. J:\structures\bridges\22 photos\HAM\IR 71\0134\Periodic inspection 10-14-2022 | Reported to District Bridge Engineer | n
C. Owens (BS1) | 2022-11-16 | periodic inspection | went down to tunnel to put chain back on dampner witch was already done. Did a walk through, there was no water anywhere at this time nor was there any alarms. the analog heat detectors in plenuim has the covers put on and the ducktape is gone. All looks good at this time.(they are doing construction at the park on top of tunnel, so intrance is fenced in) J:\structures\bridges\22 photos\HAM\IR 71\0134\Periodic inspection 11-16-2022 | Reported to District Bridge Engineer | n
Stephanie Lentz (BS2) | 2022-12-06 | Issues with Alerts from System. Receiving constant notices. | Checkde tunnel due to a steady stream of alerts. Found the dampers open over the NB lanes. Could not close through the SCADA System, had to close manually at motors. Photos at J:\structures\bridges\22 photos\HAM\IR 71\0134\Alarm Check 12-06-2022 | Reported to District Bridge Engineer | N
Stephanie Lentz (BS2) | 2022-12-08 | Check Fire Alarm System | Concerning the “Junction Box Covers”, I did not see any throughout the tunnel with tape on them. I did however find a box with 11 covers, tape attached, and 3 without tape. See photos. Also attached are photos of leakage again. Pretty good leak in the usual spots, at the wall between the lower stairs and the Plenum Room. I’ve attached photos of a new area of leakage. This is along the wall between the control room and Plenum room. Most of the leak runs along the area in the control room but I found some leakage on the west end of the dampers for NB IR71. Brandon and I discussed the cabinets in the portals for the fire extinguishers. I think we may have some issues with the locking system. A few of the cabinets had the doors open, I think the traffic is vibrating the latches loose. One in the southbound tunnel, on the east wall, has the latch broken and there is also one on the west wall of the ramp tunnel, right at the north opening that also is broken. Most of the cabinets in the south tunnel had extinguishers in the cabinets, most with an inspection date in 2021 or earlier. No extinguishers were found in the cabinets of the ramp tunnel. I just couldn’t walk the north tunnel but driving through I found the all the doors closed. I’m sure if there are extinguishers in these cabinets, they are probably past due dates on inspections. All photos can be seen at J:\structures\bridges\22 photos\HAM\IR 71\0134\Check 12-08-2022 | Reported to District Bridge Engineer
corey owens BS1 | 2023-01-03 | Issues with Alerts from System. Receiving constant notices. | Checked tunnel due to multiple alerts. Found the dampers open over the NB lanes. Could not close through the SCADA System, had to close manually at motors and when I would close them and put it back into automatic. they would automatically go back to the open position. there is running water in the stair way, right before the plenum. it is going through the door and running down the grates to the dampners on south boud. Photos at J:\structures\bridges\22 photos\HAM\IR 71\0134\Alarm and periodic | Reported to District Bridge Engineer
corey owens BS1 | 2023-02-23 | periodic inspection | Water in Plenum space room. Water ponding at bottom of the stairs in hallway to plenum space room. On the south side of plenum space there is also water leaking from the celing. A few alarms going of but all looked good.J:\structures\bridges\23 photos\HAM\IR 71\0134\2-23-23 periodic | Reported to District Bridge Engineer | N
corey owens BS1 | 3/29-3/31 and 4/11 | spring maintenance and periodic inspection | went out to meet Heath Weddle in the month of march during the spring maintenance process. There was two issues with the LHD Johnson box. (pictures of the Johnson boxes ID is in the I drive after rehab) the first issue with the LHD was one of the fiber optic cable that runs through the tunnel is broken, they was able to fix this by hooking up the other cable. the second issue is that the Johnson boxes are not communicating with the Scada system. they have to get someone that knows the specific programing of the Johnson boxes. also watched the steps taken for periodic maintenance on other parts of the system. 4/11 had to meet jeff and contractor, did a walk through still some water in the entrance. the sprocket on the north bound dampeners have been fixed, there was an trouble alarm on the fire system(sensor out of range). and the fan dampeners were stuck open. see photos J:\structures\bridges\23 photos\HAM\IR 71\0134\periodic and after spring maint. 4-11-23 | Reported to District Bridge Engineer | N
corey owens BS1 | 5/4 & 5/26 |  | 5/4 had to meet with jeff and contractor. Orr was suppose to show up to work on the Johnson boxes, and was a no show. I also brought back a new fire extinguisher. 5/26 had another meeting with contractors and all showed up and got Communication from SCADA to the Protector wire panel. also did a walk through and there is still some water in the entrance. which is the only notable problem at this moment. |  | N
corey owens BS1 | 2023-07-10 | meet altafiber | had to meet altafiber. They had to repair our phone lines to the tunnel. Which they did and added 2 new lines. Did a walk through all looked good at this time. There was a little water in the plenum-out side the electrical room. | Notified DBE. | N |  | DBE called park project above to see if they hit phone line. Assitant DBE called Altafiber to further diagnose. | Altafiber determiend break was in the park and repaired the line the same day.
corey owens BS1 | 2023-09-13 | periodic inspection | walked through today and dampner door was open along with alarms on Scada. All looked good besides the back room to plenum, behind the sub-station electrical room. There is some water poning and a little bit is entering the door jam into the electrical room. see photos J:\structures\bridges\23 photos\HAM\IR 71\0134\9-13-23 | Reported to District Bridge Engineer | N
corey owens BS1 | 10/31-11/1/2023 | periodic inspection / scada training | 10/31- walk through inspection and found water ponding in various locations, but it is happening at the same locations when it does leak.plenum by dampners and stairway. The computer room from the old bathroom was creeping out from the corner underneath the fire alarm control box. also upon arriving to the tunnel i notice that the entrance lock was broken. and on 11/1 all went down there to go over the SCADA system. | Reported to District Bridge Engineer | N
corey owens BS1 | 2023-11-20 | periodic and meet contractors | had to meet jeremy to change out the backup batteries for the johnson control boxes. Also the fire extinguishers where inspected today. Did another walk through and we have water in the same locations, with the exeption of water where the bathroom is located. (Front entrance lock was fixed) | Reported to District Bridge Engineer | N
corey owens BS1 | 2023-12-04 | periodic/check on alarms | checked on alarms and acknowledged them, everything looked fine except I did notice that fan 2 actuator 4 and 3 has a mechanical arm that has been removed and has been wired into the shut position. There was water in the same spots as last months walk through. see photos J:\structures\bridges\23 photos\HAM\IR 71\0134\periodic and acknowledge alarm 12-4-23 | Reported to District Bridge Engineer | N
corey owens BS1 | 2023-12-15 | alarms/paint calumns/walkthrough | walked through and everything is about the same as previous week, one alarm was on actuatour missing arm is why, dampners on north bound was open(I closed them), sanded and painted columns in scada room. | Reported to District Bridge Engineer | N
corey owens BS1 | 2024-01-09 | periodic inspection | rainy day so went down to water coming in at the same area(hallway and first floor with dampners). There was water coming from old bathroom, leaking into SCADA room. I cleaned trough to drain to help navigate water. That room needs cleaned out. I believe sediment build up is why water is coming into SCADA room. fan 2 actuator 4 and 3 still has a mechanical arm that has been removed and has been wired into the shut position. J:\structures\bridges\24 photos\HAM\IR 71\0134\periodic-1-9-24 | Reported to District Bridge Engineer | N
corey owens BS1 | 2024-02-05 | periodic inspection | water still at bottom of stairwell. Installed the acuator arm for fan 2 dampners back on. noticed in the electrical room the schnelder electric panel has a yellow light on that indicates SSL Tripped. I notified engineer. i also took the new keys to the local 430 fire department. J:\structures\bridges\24 photos\HAM\IR 71\0134\periodic and put actuator arm on 2-5-24 | Reported to District Bridge Engineer | N
corey owens BS1 | 4/2 & 4/3 | periodic inspection and meet with consultant | did a walk through and water was in the same areas as last walk through. They did finish the park up top. Had to meet heath down there 4/3 to go over all the wsp inpection findings that was repaired and will be repaired by this spring closing. Went through everything that was done with jeff. | Reported to District Bridge Engineer | N
Stephanie Lentz | 2024-05-17 | Periodic Inspection | Water heavy at bottom of stairwell, in plenum area and around damper for SB IR71. Water in ventilation room that has moved into fan room and can be seen around fan 1. Room with access hatch also has large amount of water with evidence of water getting into electric room. Motor for damper over NB IR71 has oil leaking. Fan 2, actuator 4 has been replaced, could be reason for alarms in SCADA. Photos can be seen at J:\structures\bridges\24 photos\HAM\IR 71\0134\5-17-2024 | Reported to District Bridge Engineer | N
Brandon Collett | 2024-05-23 | Open house for prospective maintenance contractors and subcontractors.. | Water heavy at bottom of stairwell, in plenum area and northeast corner area. Green mold is beginning to grow in the corner room. Green moss is beginning to grow under the Plenum air intake (Southeast corner). Errors encountered on SCADA. Door to SB Tunnel would not open at all. | Tried to push water to dran but drain is higher than other floor areas. Sent Email to HAM and County about possible fixes to keep water out from NW hatch door in park. It was decided to Flexseal. Sending reminder to Jeff to have door fixed by facilitiies contract. | N |  | Eric Schmidt installed Flexseal tape the following week.

## Organizaitonal Flow Chart
Organization Flow Chart Ohio Tunnel Insections
and for ODOT's only Tunnel (HAM-71-0134)
|  |  |  | Personnel | Position | Department | Email | Office Number | Cell Number | NTIS Team Leader | Certificate Provided | Date
|  |  |  | Mike Brokaw | NTIS and NBIS Program Manager, State of Ohio | ODOT Office of Structural Engineering | Michael.brokaw@dot.ohio.gov | 614.387.6210 | 614.315.7973 | yes | Yes | December, 2015
| FHWA- Program Oversight | Program Manager |  | Brandon Collett | District Structures Planning Manager | ODOT District 8 | brandon.collett@dot.ohio.gov | 513.933.6643 | 513.604.5661 | Yes | Yes | December, 2015
| Alexus Gogen | Brandon Collett (D8) |  | Joe Smithson | District Design Engineer | ODOT District 8 Engineering | joe.smithson@dot.ohio.gov | 513.933.6707 | 513.623.7349 | no
| Serge Alain Feuze lekem |  |  | Marvin Lennon | Project Engineer | ODOT District 8 Construction | marvin.lennon@dot.ohio.gov | 513.933.6129 | 513.320.5413 | no
|  |  |  | Serge Alain Feuze Lekem | Sr. Structural Engineer | FHWA Ohio Division | s.feuzelekem@dot.gov | 614.280.6845
|  | Team Leader |  | Alexis Bogen | Division Assistant Bridge Engineer | FHWA Ohio Division | alexis.bogen@dot.gov | 614.280.6847 | 561.809.3441 | no
|  | Brandon Collett (D8) |  | Wes Weir | Senior Project Manager | WSP | wesley.weir@wsp.com | 216.418.1418 | 216.278.1989 | yes
|  |  |  | Heath Weddel | Electrician | Glenwood Electric | hweddle@glenwoodelectric.com |  | 513.284.2328 | no
Engineering |  |  |  | Kyle Hendrick | Mechanical | DeBra-Kuempel | K.Kendrick@debra-kuempel.com | 513.271.6500 |  | no
Joe Smithson |  |  |  | Jeff Meyer | Assistant Structure Engineer | ODOT District 8 Structures | jeff.meyer@dot.state.oh.us | 513.933.6630 |  | Yes | Yes
|  | Team Leader Assistant |  | Justin Kemp | Hamilton County Manager | ODOT District 8 Highways | justin.kemp@dot.ohio.gov | 513.933.6120 | 513.520.3329 | no
Lighting |  | Jeff Meyer |  | Jim Bauer | Transportation Manager 3, Hamilton County | ODOT District 8 Highways | james.bauer@dot.ohio.gov | 513.933.6133 | 513.502.0449 | no
Marc Grake/Jim Judd |  |  |  | Gary Drake | Transportation Manager 2, Hamilton Cnty (Night Shift) | ODOT District 8 Highways | Gary.Drake@dot.ohio.gov | 513.933.6123 | 513.594.2137 | no
| 2023-2024 Inspect Consultant |  |  | Josh Henson | Transportation Manager 2, Hamilton County | ODOT District 8 Highways | ronald.henson@dot.ohio.gov | 513.933.6123 | 513.520.0138 | no
Construction Rehab | Wes Weir | Maintenance | District Bridge Inpectors | Chuck Hecth | Roadway Service Manager | ODOT District 8 Highways | Chuck.Hecth@dot.ohio.gov | 513.933.6523 |  | no
Marvin Lennon | Electrical Sub- Heath | Justin Kemp | Stephanie Lentz (Bridge Team Leader / BS2) | Scott Kraus | Work Zone Traffic Engineer | ODOT District 8 Construction | Scott.Kraus@dot.ohio.gov | 513.933.6519 | 513.594.4731 | no
| Mechanical Sub- | Jim Bauer | David Krazl (Bridge Team Leader / BS2) | Jon Upchurch | Traffic Management Center Specialist | ODOT CO | jon.upchurch@dot.ohio.gov | 614.387.2438 |  | no
|  | Josh Henson | Stephen Short (Bridge Specialist 1) | Darryl Meadows | Fire Specialist | Cincinnati Fire Department | darryl.meadows@cincinnati-oh.gov | 513.357.7589 |  | no
|  |  | Kristen Stacklin (Transportation Eng 2) | Robert Thomas | Cincinati Fire Department |  |  |  | 513.352.2314 | no
|  |  | Corey Owens (Bridge Specialist 1) | Monica Furr | Johnson Controls | Cincinnati Fire Department | monica.furr-ext@jci.com | 513.342.9011 |  | no
|  | Emergency Response | Eric Schmidt (Bridge Team Leader / BS2) | Robert Dewitt | Johnson Controls | Johnson Controls | robert.dewitt@jci.com |  |  | no
|  | Chuck Hecth | Dwayne Bishop (Bridge Team Specialist 1) | Stephanie Lentz | Bridge Specialist 2 | ODOT District 8 Structures | stephanie.lentz@dot.ohio.gov | 513.933.6757 | 513.441.4725 | Yes | Yes
|  |  |  | David Krazl | Bridge Specialist 2 | ODOT District 8 Structures | david.krazl@dot.ohio.gov | 513.933.6641 | 513.218.0705 | Yes | Yes
|  | Traffic Control |  | Corey Owens | Bridge Specialist 1 | ODOT District 8 Structures | corey.owens@dot.ohio.gov | 513.568.6512 | 937.733.7824 | no
|  | Scott Kraus |  | Dwayne Bishop | Bridge Specialist 1 | ODOT District 8 Structures | dwayne.bishop@dot.ohio.gov | 513.649.7650 | 513.309.2055 | no
|  |  |  | Eric Schmidt | Bridge Specialist 2 | ODOT District 8 Structures | eric.schmidt@dot.ohio.gov | 513.933.6780 | 937.416.3801 | NO
|  | Traffic Monitoring Center (TMC) |  | Stephen Short | Bridge Specialist 1 | ODOT District 8 Structures | stephen.short@dot.ohio.gov |  | 513-292-6351 | no
|  | Jon Upchurch |  | Kristen Stacklin | Transportation Engineer 2 | ODOT District 8 Structures | kristen.stacklin@dot.ohio.gov | 513.933.6642 | 513.748.4433 | no
|  |  |  | Marc Grake | Traffic Engineer | ODOT District 8 Traffic | marc.grake@dot.ohio.gov | 513.933.6607 | 513.404.8459 | no
|  | Fire Department |  | Jim Judd | Traffic Operation Manager | ODOT District 8 Traffic | jim.judd@dot.ohio.gov |  | 937.307.8490 | no
Darryl Meadows
|  | Heat Detection System |  | Consultant NTIS Team Leaders who have submitted on past Ohio Inspeciton Contracts | [8 empty] | ODOT Received (LOI Submission) | Ohio PE | NBIS
Monica Furr
|  |  |  | Personnel | Consultant | Location | Email | Office Number | Cell Number | NTIS Team Leader | Certificate Provided | Date |  | No, (MA PE) | Yes
|  |  |  | Michael Russell | Mott MacDonald | Cleveland, OH | Michael.russell@mattmac.com |  |  | ? | ? | ? |  | Yes, 77162 | Yes
|  |  |  | Henry Russell | Mott MacDonald |  |  |  |  | Yes | yes | April 24-28, 2017, Worcester, MA |  | No (Penn PE- Mech) | Yes
|  |  |  | Jeffery Long | Mott MacDonald |  |  |  |  | Yes | yes | April 18-22, 2016, Worcester, MA |  | No (MA/NY PE) | no
|  |  |  | Matt Coughlin | Mott MacDonald |  |  |  |  | Yes | yes | April 18-22, 2016, Worcester, MA |  | No (NY PE) | no
|  |  |  | Sukru Birkok | Mott MacDonald |  |  |  |  | Yes | yes | June 27-July 1, 2016, Boston MA |  | Yes
|  |  |  | Christopher Lau | Mott MacDonald |  |  |  |  | Yes | yes | June 27-July 1, 2016, Boston MA |  | Yes
|  |  |  | Ed Cinadr | Burgess & Niple | Columbus, OH | ed.cinadr@burgessniple.com | 614-459-2050 | 614-269-0522 | Yes | no | Feb 27 to March 3, 2015 (Seattle, Washington) |  | Yes
|  |  |  | Rodney Holbert | Burgess & Niple | Parkersburg, WV | rodney.Holbert@burgessniple.com |  |  | Yes | no | 2015 |  | No (Penn PE)
|  |  |  | Ncik Cioffredi | Burgess & Niple |  | Nick.Cioffredi@burgessniple.com |  |  | Yes | no | 2016, Denver Colorado |  | No (Penn PE)
|  |  |  | Jonathan McHugh | Gannett Fleming |  |  |  |  | Yes |  | 2016-02-26 |  | No (Penn PE)
|  |  |  | James Radion | Gannett Fleming |  |  |  |  | Yes |  | 2016-02-26 |  | No (Penn PE)
|  |  |  | Brain Seip | Gannett Fleming |  |  |  |  | Yes |  | 2016-02-26 |  | No (Penn PE)
|  |  |  | Paul Huffman | Gannett Fleming |  |  |  |  | Yes |  | 2016-02-26 |  | No
|  |  |  | Charles Grew | Gannett Fleming |  |  |  |  | Yes |  | 2016-02-26
|  |  |  | Ben Margerum | Gannett Fleming |  |  |  |  | Yes |  | 2016-02-26
|  |  |  | Wesley Weir | WSP Consultants | Cleveland, OH | wesley.weir@wsp.com |  |  | Yes
|  |  |  | Ken Banasak | WSP Consultants |  | kenneth.banaszak@wsp.com
|  |  |  | Aaron Campbell | WSP Consultants |  |  |  |  | Yes
|  |  |  | Justin Brelling | WSP Consultants |  |  |  |  | Yes
|  |  |  | Sandeep Tirunagari | MP Consultants |  |  |  |  | Yes
|  |  |  | Tony Federicko | WSP Consultants |  |  |  |  | Yes
|  |  |  | Stephen Mayo | WSP Consultants |  |  |  |  | Yes

## NHI Certificates
Certificates of NHI Tunnel Safety Inspection Training
| NHI Tunnel Safety Inspection Certificates | NHI Tunnel Safety Refresher Course (Required every 5 years)
ODOT Staff
Hatch Mott (Inspections 2017 thru 2020)
WSP (2021-2022)

## General Inspection Plan
General NTIS Inspection Plan:
1. | Inspect the tunnel in compliance with the National Tunnel Inspection Standards in September of Even numbered years. A minimum of two inspectors shall be certified tunnel inspectors having completed the Tunnel Safety Inspection class (FHWA-NHI-130110). The consultant shall provide inspectors names, resumes, and date of training completion for the two inspectors that will be conducting the inspections with their Letter of Interest (LOI).
2. | Provide 1 bound report and an electronic version of any deficiencies found. The report shall include color photographs imbedded within the report to demonstrate the found deficiencies. The report shall include recommendations for immediate repair (less than 1 year) and long term repairs (approximately 5 years). Approximate cost of each repair in current dollars shall be provided. Include an appendix in the back of the actual spreadsheet submission. Include a separate appendix calculating all element tunnel element quantities. Enter the data and element information into the State’s Assetwise Asset Reliability (AWAR) Inspection software by Bentley. The draft report is due 60 days after the initial tunnel inspection. The final report is due 30 days after comments are received.
3. | Inspection of the traffic portions of the tunnel shall be coordinated to coincide with weekend closures conducted by ODOT for tunnel cleaning purposes. Weekend closures are expected to begin Friday night and re-open Sunday Morning. One weekend will close the northbound tunnel. A second weekend will close the southbound bore and Third Street Exit tunnels simultaneously. Exact dates and timeframes will be determined at a later date. ODOT will provide all traffic control.