STATE OF OHIO

DEPARTMENT OF TRANSPORTATION

SUPPLEMENTAL SPECIFICATION 804

FIBER OPTIC CABLE AND COMPONENTS

January 16, 2026

804.01 Description

804.02 General

804.03 Materials

804.04 Warranties

804.05 Fiber Optic Cable

804.06 Reserved for Future Use

804.07 Reserved for Future Use

804.08 Fan-Out Kit

804.09 Drop Cable

804.10 Fiber Optic Patch Cable

804.11 Fiber Termination Panel

804.12 Fusion Splice

804.13 Fiber Optic Connectors

804.14 Splice Enclosure, Butt Style and In-Line

804.15 Reserved for Future Use

804.16 Testing

804.17 Packaging and Shipping

804.18 Fiber Optic Training

804.19 Method of Measurement

804.20 Basis of Payment

804.01 Description.  This work consists of furnishing and installing fiber optic cable and components. This specification describes the requirements for communication system cables, splicing, associated interface devices, and power cables.

804.02 General.  Furnish new materials and equipment, being of first quality, of latest design, and completely free of defects in material and poor workmanship.

Furnish materials, cables, fiber, and hardware of the same type and manufacturer to ensure uniformity, interchangeability of components, single responsibility, and most satisfactory service.

Permanently attach to each major component, the manufacturer’s name, the type or style, model number, and serial number on a weatherproof decal or tag.

Furnish cable with all fibers usable and free of surface imperfections, material and inclusions in order to meet at least 100 percent of the optical, mechanical, and environmental requirements.

Provide work that meets at least the applicable provisions of the following industry documents:

A.  U.S Department of Agriculture, Rural Electrification Administration Specification for Totally Filled Optical Fiber Cable, PE-90.

B.  EIA/TIA-455-a, Standard Test Procedure for Fiber Optic Fibers, Cables, Transducers, Sensors, Connecting and Terminating Devices, and Other Fiber Optic Components.

C.  EIA/TIA-455-25a, Repeated Impact Testing of Fiber Optic Cables and Cable Assemblies.

D.  EIA-455-28b, Method for Measuring Dynamic Tensile Strength of Optical Fibers.

E.  EIA-455-33a, Fiber Optic Cable Tensile Loading and Bending Test.

F.  EIA-455-34, Interconnection Device Insertion Loss Test.

G.  EIA-455-41, Compressive Loading Resistance of Fiber Optic Cables.

H.  EIA/TIA-455-81a, Compound Flow (Drip) Test for Filled Fiber Optic Cable.

I.  EIA/TIA-455-82b, Fluid Penetration Test for Fluid-Blocked Fiber Optic Cable.

J.  EIA-455-89a, Fiber Optic Cable Jacket Elongation and Tensile Strength.

K.  EIA-455-95, Absolute Optical Power Test for Optical Fibers and Cables.

L.  EIA-455-104, Fiber Optic Cable Cyclic Flexing Test.

M.  EIA/TIA-598, Color Coding of Fiber Optic Cables.

N.  EIA/ANSI-472 Generic Requirement for Optical Fiber and Optical Fiber Cables.

O.  ANSI/ICEA S-87-640.

P.  ANSI/TIA/EIA-526-7: OFSTP-7 Measurement of Optical Power Loss of Installed Single-Mode Fiber Cable Plant.

804.03 Materials.  Furnish materials conforming to 904 and as listed on the Department’s Traffic Authorized Products (TAP) List. Provide all materials required for the installation and splicing of the specified communications cables, power cables, and associated interface devices. Furnish materials, cables, fiber, and hardware that is commercially-available items.

804.04 Manufacturer Warranties. Provide a three year manufacturer’s warranty to all items contained in this specification with the exception of fiber optic cable, that is warranted by the manufacturer for a period of 25 years. This 25 year transferrable warranty covers the cable against significant degradation of the fiber caused by cable defects incurred only during the manufacturing process and does not cover connectivity to other fiber cable or components.  In order to guarantee the ability of the manufacturer to provide the required warranty the contractor shall be a certified installer of the manufacturer and be listed on ODOT’s prequalification list for Work Type 55, Fiber Optic Installation, Splicing, Termination and Testing.

804.05 Fiber Optic Cable. Furnish fiber optic cable that conforms to 904.01 or 904.02 and is listed on the Department’s TAP.

Provide written manufacturer certification that the offered cable complies with all optical, electrical and mechanical requirements set forth in this and all referenced specifications.

Ensure any deviation of the offered cable from the requirements is conspicuously noted by colored highlights, callout bubbles, or both in the submitted material documentation.

Provide cables are free of material or manufacturing defects and dimensional non-uniformity that would:

5. Interfere with the cable installation using acceptable installation practices.

6. Degrade the transmission performance and environmental resistance after installation.

7. Inhibit proper connection to interfacing elements.

8. Otherwise yield an inferior or inoperative installation.

804.05.A.  Cable Wraps. Furnish and install cable wraps (markers) on the fiber optic cable installed in each pull box (median and round).

Provide wraps that:

- Are 4 in (101.6 mm) long “snap on type”, UV stabilized, and solid color throughout.

2.	The wording includes no advertising logo or message.

Provide wraps with color and text as follows:

- For ODOT cable: yellow background with black print text “ODOT fiber optic cable – ITS 614-387-4113”.

Include the fiber count of the appropriate fiber that the cable wraps are placed upon.

804.05.B. Cable Installation.  The cable shall be installed in continuous lengths from splice point to splice point as per the plans. Exercise extreme caution when ordering cable in order to ensure that no additional splicing, beyond that indicated by the plans, is required.

If it is believed that additional splices are required, immediately notify the Engineer for resolution.

Certification is required by the cable manufacturer to perform installation with the cable manufacturers recommended procedures including at least the following:

- Proper attachment to the cable strength elements for pulling during installation.

- Cable tensile limitations and the tension monitoring procedures.

- Cable bending radius limitations.

Submit documentation to the Engineer showing that one of the following certifications is held at the time of the contract letting date:

- Building Industry Consulting Service International (BICSI) – All fiber installers must be Installer 2, Optical Fiber certified and at least one installer BICSI Technician certified and the BICSI Technician designated to oversee all fiber optic cable operations.

- Electronics Technician Association (ETA) – All fiber installers must be FOI certified and at least one installer FOT-OSP certified and all fiber optic cable operations overseen by the FOT-OSP Technician.

- Fiber Optic Association (FOA) – All fiber installers must be CFOT certified and at least one installer shall be CFOS certified and the CFOS assigned to oversee all fiber projects.

Furnish certification to the Engineer prior to installing any cable.

Comply with the cable manufacturer’s specifications at all times.

Do not exceed the pulling tension and bending radii limitation for optical fiber cables under any circumstances.

Use large diameter wheels, pulling sheaves, and cable guides to maintain the appropriate bending radius.

Provide tension monitoring at all times during the pulling operation by using commercial dynamometers, load cell instruments, or shearing pins.

804.05.B.1. Air-blown/Pushable Fiber Optic Cable Installation. Follow all manufacturer recommended procedures when performing installation of air-blown fiber. Have a manufacturer representative present for the installation of the first two complete runs of the air-blown fiber optic cable from pull-box to pull-box.

804.05.B.2. Slack Installation. The Department will require proper storage of slack cable, both long term and short term.

Do not leave slack cable lying free on the ground or floor of a building except during the actual pulling process.

Neatly coil the cable, adhering to the bend radius requirements as directed by the Engineer.

Submit certified shop drawings of the materials and installation of the aerial hardware conforming to 625.06.

The fiber optic cable used in the slack installation (both aerial and underground) and mounting hardware is included with the quantity for the fiber optic cable.

804.05.B.2.A. Underground Slack Installation.  In underground installations, coil 150 ft (45.72 m) of fiber slack in each 48 in or 32 in (1.22 m or 0.81 m) pull box.  The slack coil should be easily removed from the pull box and not have other cables passing through the coil.  If the Engineer determines the slack is not stored properly, remove and reinstall the fiber, other cables, or both in conflict to the satisfaction of the Engineer at no cost to the Department.  Notify the Engineer if this amount of slack is not capable of being stored and the Engineer will provide direction.

804.05.B.2.B. Aerial Slack Installation.  Where slack installation is designated, but a splice enclosure is not designated, provide a 150 ft in-line aerial mounted slack cable installation.

Where an aerial splice enclosure is shown, provide 150 ft (75 ft prior, 75 ft after) of aerial mounted slack for trunk cable entering the splice enclosure. Provide 75 ft of slack for the drop cable.

Where the fiber cable is being brought aerially into an underground installation, provide 150 ft of slack for each cable run entering the designated pull box, or as directed by the Engineer.  The slack coil should be easily removed from the pull box and not have other cables passing through the coil.  If the Engineer determines the slack is not stored properly remove and reinstall the fiber, other cables, or both in conflict to the satisfaction of the Engineer at no cost to the Department.

804.08 Fan-Out Kit.  Fan out and apply connectors to all drop cable fibers as specified in the termination details, or as directed by the Engineer, and insert them into the termination panel.  Color coded, Pre-connectorized, pre-tested pigtails may also be used.

Connectors attached to fibers from the fan-out kit are incidental to the fan-out kit.

804.09 Drop Cable.  Drop cables are used to connect the fiber trunk cable to termination point.

Leave unused drop cable buffer tubes and fibers for future use.

Place spare drop cable fibers at the splice enclosure end inside of the enclosure with sufficient excess to provide at least two service loops.  Remove at least 10 ft (3.05 m) of outer jacket to accomplish this.

Terminate drop cable fibers and buffer tubes at the termination panel or leave coiled for future use as detailed in the fiber termination drawings, or as directed by the Engineer.

Provide strain relief (cable support assembly) for drop cables routed down through/on a pole from aerial interconnect.

Cost of the cable support assembly is incidental to the bid item price of the drop cable.

Store all drop cable slack underground in the nearest pull box.

To provide strain relief for the termination panel, and to help protect the cable from accidental pulling, secure drop cable to the rack, cabinet, or wall using a tie wrap, or as directed by the Engineer.

Ensure any means of securing the cable does not apply stress to the drop cable.

804.10 Fiber Optic Patch Cable.  Provide patch cables for connections to the fiber termination panels from optical equipment.

Provide patch cable connectors that match the connectors of the termination panel and optical equipment.

Use patch cables that are duplex unless otherwise directed by the Engineer.

Furnish patch cable connector polish that is UPC unless otherwise directed by the Engineer.

Furnish patch cords that are 9.84 ft (3 m) in length unless otherwise directed by the Engineer.

804.11 Fiber Termination Panel.  Use a termination panel listed on the TAP.  House in the termination panel all fiber optic pigtails, fiber optic connectors/connector modules, fiber optic patch cords, and splice trays.

All fiber optic pigtails, fiber optic connectors, fiber optic patch cords, splice trays, external strain relief, pigtails, and fusion splices are incidental to the unit cost of the fiber optic termination panel.

Provide pigtails that are 13.12 ft (4 m) in length unless otherwise directed by the Engineer.

Provide duplex 9.84 ft (3 m) patch cables of the appropriate fiber type and fiber connector in a quantity that is half of the number of fiber optic connectors available on the termination panel, or as directed by the Engineer.

Install fiber and splice trays in the following manner:

- Secure fiber entering the termination panel to an external strain relief bracket.

- Route buffer tubes as they enter the termination panel to ensure no kinks, binds, pinches, or extreme bends are introduced.

- The Department considers the termination panel unacceptable if any buffer tube is kinked or damaged.  Correct, at no cost to the Department, as directed by the Engineer.

- Ensure all buffer tubes and pigtails enter the splice tray on the same side.

- Remove at least 10 ft (3.05 m) of outer jacket from the fiber optic cable entering the termination panel.  Remove at least 2 ft (0.61 m) of buffer tube to expose the bare fibers inside that will be contained by the splice tray.  Coil the remaining buffer tube inside the termination panel to provide service loops for future maintenance.

- Remove at least 2 ft (0.61 m) of outer jacket from the pigtail(s) to expose the bare fibers inside that will be contained by the splice tray.  Coil the remaining pigtail inside the termination panel to provide service loops for future maintenance.

- Protect all fusion splices by a heat shrink splice sleeve with a stainless steel rod and secure in the splice tray in a splice sleeve holder

Install the termination panel in the cabinet as described below:

804.11.A. NEMA Cabinet.  Utilize a termination panel listed on the TAP.  Attach termination panel to the inside wall of the cabinet.

804.11.B. Caltrans Signal Cabinet (332, 336).  Utilize a 19-inch rack mount termination panel listed on the TAP

804.11.C. Caltrans (334) or AASHTO/ITE/NEMA ITS Cabinet.  Utilize a 19-inch rack mount termination panel listed on the TAP for Cabinet use.

Mount the termination panel per the ITS Standard Construction Drawings.

Install all fiber optic cable, buffer tubes, pigtails, patch cords, and splice trays in a neat and orderly fashion and secure to eliminate any interference with the removal, replacement, operation, and maintenance of all other items located in the cabinet.

Perform all splicing based on fiber termination drawings found in the plan set, or as directed by the Engineer.

804.11.D.	Data Center. Utilize a 19-inch rack mount termination panel listed on the TAP for Data Center use.

Install all fiber optic cable, buffer tubes, pigtails, patch cords, and splice trays in a neat and orderly fashion and secure to eliminate any interference with the removal, replacement, operation, and maintenance of all other items located in the rack.

Perform all splicing based on fiber termination drawings found in the plan set, or as directed by the Engineer.

804.12 Fusion Splicing.  All splices shall be performed using a core aligning fusion splicer or a mass (ribbon) fusion splicer.  Use of single fiber cladding alignment splicers is not permitted.

Splice only at locations identified in the plans, or as directed by the Engineer.

Splice fibers as specified in the termination details, splice enclosure details, or as directed by the Engineer.

Ensure all splicing equipment is in good working order, properly calibrated, and meets all industry standards and safety regulations.  Provide calibration data to the Engineer upon request.

Perform cable preparation, closure installation, and splicing in accordance with accepted and approved industry and manufacturer standards in addition to the Department’s standards.

Upon completion of the splicing operation, deposit all waste material in suitable containers, removed from the job site, and disposed of in an environmentally acceptable manner.

Ensure compliance with TIA-568.3-D. Additionally, no individual splice loss measured in a single direction shall exceed 0.2 dB.  Do not exceed 0.05 dB for the estimated loss as read by the fusion splicer.

804.13 Fiber Optic Connectors.

Provide optical fiber connectors as required for the equipment and termination panel.

Connectors shall be pigtailed or splice on style.  The Engineer may allow the use of other style connectors in unique cases where pigtailed or splice on style connectors are not suitable.

804.14 Splice Enclosure, Butt Style and In-Line.   Use a splice enclosure listed on the TAP.  Perform cable preparation as described below.

- Use ring cut methodology.

- Cut back trunk cable jacketing at least 20 ft (6.1 m) to allow buffer tubes to be stored uncut/unopened with at least two service loops inside the enclosure.

- Open the trunk cable buffer tube that is to be spliced and expose at least 4 ft (1.22 m) of the bare fibers.  Cut the bare fibers at the midpoint (at least 2 ft (0.61 m) on each side after the cut) to splice on to the drop cable.

- Provide drop cable(s) that have at least 10 ft (3.05 m) of outer jacket removed and 2 ft (0.61 m) of buffer tube removed to expose the bare fibers.

- Ensure all buffer tubes enter the splice trays on the same side.

- Ensure the remaining trunk cable fibers in the opened tube remain uncut and stored in the splice tray.

- The only trunk cable fibers that are to be cut are the trunk cable fibers being spliced to the drop cable.

- Cost for the splices, splice trays, and other materials are incidental to the fiber optic cable being spliced. If all fiber optic cable is existing, then splices will be itemized separately.

The Engineer may allow a full cut of the trunk cable at the splice enclosure location. Obtain written permission from the Engineer before proceeding with this method.  The additional splices, splice trays, and other materials are incidental to the cost of the splice enclosure.

804.15 For future use

804.16 Testing.  All testing listed below is incidental to the cost of new fiber optic cable and completed and approved, prior to acceptance of the fiber optic cable by the Engineer.

The testing listed below may also be used to check if existing cable is still suitable for use. If this is the case, the item will be paid as a lump sum (Item 804E38000).

804.16.A.  Pre-Installation Testing (Factory and Reel Testing).  Obtain factory test data sheets for each reel of optical fiber cable delivered.

Test each reel using an Optical Time Domain Reflectometer (OTDR) to prove no damage was incurred during shipping / transportation and all fibers meet the applicable specifications.

If requested provide the factory test results and the pre-installation reel test results to the Engineer prior to installation as part of final acceptance of the section of cable for payment.

804.16.B. Post-Installation Testing.  Test all fibers with an Optical Time Domain Reflectometer (OTDR).

Coordinate with the Engineer for specific locations for the testing.

Provide the Engineer written notification at least 14 calendar days before testing the fiber optic cable.

Do not begin testing until written authorization and fiber locations and test points have been received from the Engineer.

Perform tests as described below:

1.	Post-Installation Testing when splicing and terminating was performed

Test all single mode fiber cables at both 1310 nm and 1550 nm after installation.  Perform bidirectional testing.  Use a launch cable of at least 100 meters.

Fibers will be considered acceptable if the OTDR trace for that fiber shows an end to end loss of less than:

xx dB + yy (0.2)dB

yy = the number of splices

xx = (length of run) * (fiber attenuation at the specified wavelength)

In addition to the requirements of TIA-568.3-D no individual splice may show a loss of greater than 0.2 dB regardless of the total accumulated attenuation of the fiber.

Perform any additional tests required by the ANSI/TIA/EIA standard and include in the written test report.

2.	Post-Installation Testing when no splicing and terminating was performed (Bare fiber testing)

Test all single mode fiber cables at both 1310 nm and 1550 nm after installation.  Unidirectional testing is acceptable.  Use a launch cable of at least 100 meters.  Provide actual cable footage marks for beginning and end of each cable run to verify lengths given by OTDR.

Fibers will be considered acceptable if the OTDR trace for that fiber verifies the cable footage marks provided for the run, the attenuation matches the intrinsic attenuation of the fiber for the tested wavelengths and length of run, and no attenuation is shown that correlates to bending losses (improper installation with bend radius exceeded) or other cable damage from installation.

Perform any additional tests required by the ANSI/TIA/EIA standard and include in the written test report.

Test each fiber strand as specified above.  Overall, the OTDR test results are made up of the wavelength of the conducted test, the link length, attenuation, cable identification, and the locations of the near end, the far end and each splice point or points of discontinuity.  Test names for near end and far end shall be descriptive and clear to the test reviewer.  Names shall include a site name as provided by the Engineer, stationing or mile marker of test location, and cardinal direction of the test.

Submit electronic format results for each fiber strand as part of the final documentation, prior to acceptance. Each test result must clearly identify which fiber was tested using the naming conventions above.

Submit to the Engineer all test results in electronic format provided by the manufacturer of the test equipment used to perform the tests.

Provide the results so they can be viewed without the use of special software or additional equipment, unless the software or equipment is also delivered to the Engineer.

If software is provided, a separate pdf document showing all fiber test results must be submitted to be placed in the project file.

Any software or equipment delivered will become the permanent property of the maintaining agency and will not be returned.

If a fiber or cable fails to meet the above requirements, replace or correct at no expense to the Department.

Test results include a record of wavelength, fiber type, fiber and bundle number, test equipment and model number, date reference setup, and operator (crew members).

In the event that test results are not satisfactory perform corrective work as directed by the Engineer.  After corrective work is completed perform additional tests as directed by the Engineer.

The Engineer will require the permission and presence of the Contractor prior to allowing tests related to connected equipment of others. Perform only that testing required to prove that the fiber connections are correct.

804.17 Packaging and Shipping.  Package the completed cable for shipment on wooden reels.

Wrap the cable and reel in a water resistant covering.

Securely fasten each end of the cable to the reel to prevent the cable from coming loose during transit.

At least 6 ft (1.83 m) of cable length on each end of the cable shall be accessible for testing.

Seal both ends of the cable to prevent the ingress of moisture.

Provide on each cable reel a durable weatherproof label or tag showing the manufacturer's name, the cable type, and the actual length of cable on the reel, the Contractor's name, the contract number, and the reel number.

Include a shipping record in a weatherproof envelope showing the above information and also include the date of manufacture, cable characteristics (size, attenuation, etc.), cable identification number and any other pertinent information.

Furnish a reel with at least a diameter of thirty times the diameter of the cable.

Furnish the optical fiber cable in one continuous length per reel with no factory splices in the fiber.

Mark each reel to indicate the direction the reel and rolled to prevent loosening of the cable.

Furnish installation procedures and technical support information at the time of delivery.

## 804.18 Fiber Optic Training. Provide both formal classroom and "in-field" operations and maintenance training for up to 20 designated personnel on the fiber optic cable system and its components.  Coordinate all training at a mutually agreed upon time and location.  Provide training material generated for each course with "hand-outs" for each attendee.  Provide hand-outs that serve not only as subject guidance, but as quick-reference material for future use.  Deliver all course material, in reproducible form, to the Engineer immediately following course completion.  Provide two DVD copies of the training program.

Submit for Engineer’s approval at least two weeks prior to the proposed starting date, the schedule for such training.

## 804.18.A. Classroom Training.  Train personnel to install, splice, and test fiber optic cable.  Provide training of at least 32 hours.  Provide 32 hours of fiber optic training in a four day course taught by personnel from the manufacturer of the fiber optic cable.  Include at least the following topics in the course: safety, theory, fiber types, cable placement techniques, fiber optic sheath removal, hardware types, fault location with an Optical Time Domain Reflectometer (OTDR), Dense Wave Division Multiplexing (DWDM), splicing and termination methods and applications, theory and principles of splicing, fusion splicing, mechanical splicing, cable preparation procedures for installing optical connectors, installing connectors, mocking up a typical traffic control system, cable system testing and documentation, attenuation test procedures, and overall cable system  maintenance.  Include lectures, demonstrations, and hands-on experience with the equipment.  Provide students hand-outs to use as guides for field applications.

## 804.18.B. Field Training.  Provide field training.  Provide training consisting of at least the following: eight hours of fiber optic communications plant trouble shooting including fault location using an optical power meter/light source and using an Optical Time Domain Reflectometer (OTDR) cable tester, four hours of field splicing (that includes re-enterable rotary mechanical splicing (for emergency temporary repair) and fusion splicing techniques), and four hours of training on the installation, maintenance, and replacement of fiber interconnect centers.

## 804.18.C. Course Outline and Workbooks.  For both types of training, submit four copies of all proposed training material for approval, and include course curriculums, draft manuals, and resumes of instructors.  Furnish submittals to the Engineer at least four weeks prior to the scheduled starting date.   For the classroom training, provide for each participant a course workbook in loose-leaf format in a three ring binder.

804.19 Method of Measurement.  The Department will measure Fiber Optic Cable by the number of feet, including slack, and will include the costs for equipment, fusion splices, labor and miscellaneous materials.

The Department will measure Fiber Optic Cable, Airblown / Pushable by the number of feet, including slack, and will include the costs for equipment, fusion splices, labor and miscellaneous materials.

The Department will measure Fan-Out Kit by the number of each, and will include all costs for material, equipment, tools and labor to provide and install the fan-out kit.

The Department will measure Drop Cable by the number of each or by the number of feet, depending on the pay item used, and will include all slack, costs for material, equipment, tools and labor to provide and install the drop cable.

The Department will measure Fiber Optic Patch Cable by the number of each and will include supplying and installing connectors on all ends of the patch cable.

The Department will measure Fiber Termination Panel by the number of each, and will include all materials, MTP Module, splice trays, pre-terminated MTP cables, patch cables, tools and labor to provide and install a termination panel.

The Department will measure Fusion Splice by the number of each, and will include all costs for equipment, material and labor to provide a permanent fused splice including splice protection.

The Department will measure Fiber Optic Connector by the number of each.

The Department will measure Splice Enclosure by the number of each and will include fusion splices and aerial or pull box wall mounting brackets as required.

The Department will measure Fiber Optic Training by the number of each.

804.20 Basis of Payment.  The Department will pay for accepted quantities at the contract prices as follows:

Item 	Unit 		Description

804 	Foot	 	Fiber Optic Cable, _____ Fiber

804		Foot		Fiber Optic Cable, Airblown / Pushable, _____Fiber

804 	Each 		Fan-Out Kit, _____ Fiber

804 	Each		Drop Cable, _____ Fiber

804 	Foot		Drop Cable, _____ Fiber

804 	Each 		Fiber Optic Patch Cable, _____ Fiber

804 	Each 		Fiber Termination Panel, _____ Fiber

804 	Each 		Fusion Splice

804 	Each 		Fiber Optic Connector

804 	Each 		Splice Enclosure

804		Each		Fiber Optic Training

Designer Note: This specification shall be used for any project that contains Intelligent Transportation System (ITS) Devices and Components.