## A
Voltage Drop Calculation
|  |  | Section |  |  |  |  | Current (Amperes) |  | Voltage Drop
|  |  | From | To | Length (ft) | AWG | Resistance (Ohms/Kft) | At Point | Accum | In Section | Accum | % Drop | Power Loss (W/ft) | At Point
ENTER INFORMATION: |  |  | LP-A2 | LP-A1 | 174 | 10 | 1.2 | 0.64 | 0.64 | 0.26726 | 0.75 | 0.31 | 0.00098304 | LP-A2 | Amp Calc | P = I * V
Project: | CUY-480 |  | LP-A1 | PB-A1 | 112 | 10 | 1.2 | 0.64 | 1.28 | 0.34 | 0.49 | 0.2 | 0.0029259 | LP-A1 |  | I = P/V
Site #: | 115826 | [13 empty] | Watts | 51
Location: | W 220th Street Bridge |  | LP-B2 | LP-B1 | 139 | 10 | 1.2 | 0.64 | 0.64 | 0.2135 | 0.71 | 0.29 | 0.00098304 | LP-B2 | Voltage | 120
Power Service: | Pole at STA. 12+2.48 |  | LP-B1 | PB-A1 | 114 | 10 | 1.2 | 0.64 | 1.28 | 0.35 | 0.49 | 0.2 | 0.002948 | LP-B1 | Amps | 0.425
Circuit: | N (Legs A and B)
Sheet #: | xx (LP101) |  | PB-A1 | EX-LP (PS) | 23 | 10 | 1.2 | 0 | 2.56 | 0.14 | 0.14 | 0.06 | 0 | PB-A1
| Wire Size (AWG) | Resistance (Ohms/Kft)
| 12 | 2.05
| 10 | 1.2
| 8 | 0.809
| 6 | 0.51
| 4 | 0.321
| 3 | 0.254
| 2 | 0.201
| 1 | 0.16
| 1/0 | 0.127
| 2/0 | 0.101
| 3/0 | 0.0797
| 4/0 | 0.0626
Voltage Drop Equations:
Voltage drop in circuit section = (V)
- length includes the length of section with 5-10 ft added to each end, then round up to the closest increment of 5 ft.
)
& Drop = (%)
Power Loss =
Wire Data from 2011 Edition of National Electrical Code, Chapter 9 Table 8
Voltage Drop Equations:
Voltage drop in circuit section =(2∗𝐼∗𝑙∗𝑅" " )/1000 (V)
𝐼=𝐴𝑐𝑐𝑢𝑚𝑢𝑙𝑎𝑡𝑒𝑑 𝐶𝑢𝑟𝑟𝑒𝑛𝑡 𝑖𝑛 𝑆𝑒𝑐𝑡𝑖𝑜𝑛 (𝐴)
𝑙=𝐿𝑒𝑛𝑔𝑡ℎ 𝑜𝑓 𝑠𝑒𝑐𝑡𝑖𝑜𝑛 (𝑓𝑡)
- length includes the length of section with 5-10 ft added to each end, then round up to the closest increment of 5 ft.
𝑅=𝑅𝑒𝑠𝑖𝑠𝑡𝑎𝑛𝑐𝑒 𝑜𝑓 𝑤𝑖𝑟𝑒 (𝛺/1000𝑓𝑡)
& Drop = (𝐴𝑐𝑐𝑢𝑚𝑢𝑙𝑎𝑡𝑒𝑑 𝑉𝑜𝑙𝑡𝑎𝑔𝑒 𝐷𝑟𝑜𝑝)/(𝑆𝑢𝑝𝑝𝑙𝑦 𝑉𝑜𝑙𝑡𝑎𝑔𝑒)∗100 (%)
Power Loss = (𝑣𝑜𝑙𝑡𝑎𝑔𝑒 𝑑𝑟𝑜𝑝 𝑖𝑛 𝑠𝑒𝑐𝑡𝑖𝑜𝑛∗𝑐𝑢𝑟𝑟𝑒𝑛𝑡 𝑎𝑡 𝑝𝑜𝑖𝑛𝑡)/(𝑙𝑒𝑛𝑔𝑡ℎ ) (𝑤𝑎𝑡𝑡𝑠/𝑓𝑡)
Wire Data from 2011 Edition of National Electrical Code, Chapter 9 Table 8
Directions:
1. Fill out all cells under Enter Information:
2. Fill out anything that is bolded in the table
3. Select the corresponding cable size (AWG) so the voltage drop is less than 5%