## Joint Restaint Calcs
lock/unlock password: gpd
Ductile Iron Pipe Joint Restaint Calculations
Pipe/Installation Properties
| DIP Pipe Size: | 12 | in
| Design Pressure: | 350 | psi
| Pipe OD: | 1.1 | in
| Pipe Cross Sectional Area: | 136.8 | in
| Pipe Weight/Ft: | 39 | lbs/ft
| Water Weight/Ft: | 53 | lbs/ft
| Depth of Cover: | 5 | ft
| Polyethylene Encased: | No | (Y/N)
| Soil Type: | Good Sand and Gravel
| Laying Condition: | 4
| Kn: | 0.85
| Angle 1: | 36
| F | 0.8
| C | 0
| fc | 0
| gamma | 100
Frictional Resistance Calc:
| Fs = | 654.912 | lbs/ft
| Pp = | 2131.8898
Horizontal Fitting Restraint Length: |  |  |  | Vertical Fitting Restraint Length:
| Fitting | Restraint Length |  | Fitting | Restraint Length
| 11.25 | 4.2808 |  | 11.25 | 10.7954
| 22.5 | 8.6454 |  | 22.5 | 21.8021
| 45 | 18.0023 |  | 45 | 45.3986
| 90 | 43.4513 |  | 90 | 109.5763
*restraint length listed is for each side of the bend. Total restraint length should be doubled, centered on the fitting.

## Reference
Polyethylene Encased | Soil Type | Laying Type
Yes | Clay 1 | 2
No | Silt 1 | 3
| Clay 2 | 4
| Silt 2 | 5
Coh-gran
Sand Silt
Good Sand and Gravel

## Kn
| 2 | 3 | 4 | 5 | angle 1 | f | C | fc | gamma | lay condition 2 f | lay condition 2 fc
Clay 1 | 0.2 | 0.4 | 0.6 | 0.85 | 0 | 0 | 300 | 0.8 | 90 | 0 | 0.5
Silt 1 | 0.2 | 0.4 | 0.6 | 0.85 | 29 | 0.75 | 0 | 0 | 90 | 0.5 | 0
Clay 2 | 0.4 | 0.6 | 0.85 | 1 | 0 | 0 | 300 | 0.8 | 90 | 0 | 0.5
Silt 2 | 0.4 | 0.6 | 0.85 | 1 | 29 | 0.75 | 0 | 0 | 90 | 0.5 | 0
Coh-gran | 0.4 | 0.6 | 0.85 | 1 | 20 | 0.65 | 200 | 0.4 | 90 | 0.4 | 0.4
Sand Silt | 0.4 | 0.6 | 0.85 | 1 | 30 | 0.75 | 0 | 0 | 90 | 0.5 | 0
Good Sand and Gravel | 0.4 | 0.6 | 0.85 | 1 | 36 | 0.8 | 0 | 0 | 100 | 0.75 | 0

## Pipe Table
Pipe Diameter | Pressure | Pipe OD | Cross sectional Area | Weight/ft Pipe | Weight/ft Water | Weight/ft Total
3 | 350 | 0.33 | 12.3 | 10 | 4 | 14
4 | 350 | 0.4 | 18.1 | 12 | 6 | 18
6 | 350 | 0.58 | 37.3 | 18 | 13 | 31
8 | 350 | 0.75 | 64.3 | 24 | 24 | 48
10 | 350 | 0.93 | 96.7 | 30 | 37 | 67
12 | 350 | 1.1 | 136.8 | 39 | 53 | 92
14 | 250 | 1.28 | 183.8 | 47 | 72 | 119
16 | 250 | 1.45 | 237.7 | 57 | 94 | 151
18 | 250 | 1.63 | 298.6 | 66 | 119 | 185
20 | 250 | 1.8 | 366.4 | 78 | 147 | 225
24 | 200 | 2.15 | 5227 | 93 | 212 | 305
30 | 150 | 2.67 | 804.2 | 123 | 329 | 452
36 | 150 | 3.19 | 1152 | 163 | 473 | 636
42 | 150 | 3.71 | 1555.2 | 206 | 642 | 848
48 | 150 | 4.23 | 2026.8 | 261 | 838 | 1099
54 | 150 | 4.8 | 2602.1 | 325 | 1078 | 1403
60 | 150 | 5.13 | 2981.2 | 371 | 1237 | 1608
64 | 150 | 5.47 | 3387 | 410 | 1407 | 1817