Customer Installed Conduit for Duke Energy Lighting Midwest

Thank you for choosing Duke Energy as your lighting provider. You have chosen to install your own conduit system for this project. Below you will find the standards for which this system must by constructed. Duke Energy will provide you with a layout for the conduit system and the system must be built to the specifications listed below and at the locations provided by Duke Energy.  Once the conduit system has been completely installed and Duke has started construction of the lighting project you will be responsible for responding to any issues that might arise during construction within a 24-hr. time frame from the time of notification. If corrections cannot be made, and there is no other work that Duke can perform while waiting on corrections to the customer installed conduit system Duke may need to pull off the project until corrections are made. If this is the case the project will be rescheduled as soon as the schedule permits, and re-mobilization charges may apply.  Examples of issues with conduit system could be, but not limited to, broken duct, duct in wrong location, duct at incorrect depth.

CUSTOMER RESPONSIBILITIES

-THE CONDUIT DESIGN WILL BE PROVIDED BY THE DUKE ENERGY DESIGNER. THE DESIGN WILL SHOW THE LOCATION WHERE ALL FACILITIES

(CONDUIT, PEDESTALS, TRANSFORMERS, POLES, ETC.) WILL BE INSTALLED. ANY PROPOSED CHANGES IN THE CONDUIT DESIGN MUST BE REVIEWED AND APPROVED BY THE DUKE ENERGY DESIGNER PRIOR TO INSTALLATION.

-PROVIDE ALL MATERIAL RELATED TO THE CONDUIT SYSTEM AND THE LABOR TO INSTALL THIS MATERIAL.

-INSPECT THE CONDUIT SYSTEM AND CORRECT ALL INSTANCES OF NON-COMPLIANCE WITH THE REQUIREMENTS.

-COMPLY WITH ALL REQUIREMENTS LISTED IN THIS DOCUMENT.

DUKE ENERGY RESPONSIBILITIES

-THE CONDUIT DESIGN WILL BE PROVIDED BY THE DUKE ENERGY DESIGNER. THE DESIGN WILL SHOW THE LOCATION WHERE ALL FACILITIES

(CONDUIT, PEDESTALS, TRANSFORMERS, POLES, ETC.) WILL BE INSTALLED. ANY PROPOSED CHANGES IN THE CONDUIT DESIGN MUST BE REVIEWED AND APPROVED BY THE DUKE ENERGY DESIGNER PRIOR TO INSTALLATION.

-PROVIDE ALL CABLE AND ASSOCIATED LIGHTING MATERIALS ALONG WITH THE LABOR TO INSTALL THESE MATERIALS.

-DUKE ENERGY RESERVES THE RIGHT TO REFUSE ACCEPTANCE OF ANY PORTION OF A CONDUIT SYSTEM THAT DOES NOT MEET ALL OF THE REQUIREMENTS LISTED IN THIS DOCUMENT. IT WILL BE THE CUSTOMER'S RESPONSIBILITY TO CORRECT ALL INSTANCES OF NON-COMPLIANCE.

-ONCE ALL CABLE AND EQUIPMENT HAVE BEEN INSTALLED, DUKE ENERGY WILL MAKE ANY NECESSARY FUTURE REPAIRS OR ALTERATIONS TO THE CONDUIT SYSTEM AT ITS EXPENSE.

TRENCH REQUIREMENTS

-THE UNDERGROUND TRENCH CONTAINING ELECTRIC CABLES IS FOR THE SOLE USE OF DUKE ENERGY. NO OTHER UTILITIES OR FACILITIES FOR IRRIGATION, PRIVATE LIGHTING, SECURITY, PLUMBING, OR ANY OTHER PURPOSE MAY BE INSTALLED IN THE TRENCH WITHOUT THE EXPRESS PERMISSION OF DUKE ENERGY.

-THE BOTTOM OF THE TRENCH MUST BE SMOOTH AND FREE OF ROCKS, ROOTS, CONSTRUCTION DEBRIS OR ANY OTHER HARD OR SHARP OBJECT. IF NECESSARY, INSTALL A FEW INCHES OF CLEAN BACKFILL TO COVER ANY OF THESE ITEMS THAT CANNOT BE REMOVED.

-ALL BACKFILL MUST BE FREE OF ROCKS, CONSTRUCTION DEBRIS, OR ANY OTHER HARD OBJECTS.

-THE CUSTOMER WILL BE RESPONSIBLE FOR ANY SETTLING OR WASHOUT OF THE TRENCH.

-ALL CONDUIT MUST BE INSTALLED AT THE PROPER DEPTH WITH A MINIMUM COVER OF 30”.

-THE MAXIMUM TRENCH DEPTH MUST NOT EXCEED THREE (3) FEET

MATERIAL REQUIREMENTS

-PVC CONDUIT AND CONDUIT FITTINGS MUST BE SCHEDULE 40 OR GREATER, RATED FOR USE WITH 90° C ELECTRICAL CABLE, UL LISTED

AND GRAY IN COLOR. NO WATER, SEWER, GAS OR TELECOMMUNICATION PIPE MAY BE USED. EACH LENGTH OF CONDUIT AND EACH

BEND MUST HAVE AN INTEGRAL BELL ON ONE END. THE CONDUIT MANUFACTURER'S NAME, CONDUIT SIZE, TYPE AND DATE CODE MUST

BE PRINTED ON THE SURFACE OF THE CONDUIT.

-FOR JOBS INSTALLED VIA DIRECTIONAL DRILLING HDPE CONDUIT MUST BE SDR 13.5 OR GREATER, RATED FOR USE WITH 90°C ELECTRICAL CABLE, AND BLACK WITH EITHER 3 OR 4 RED STRIPES OR TOTALLY RED. THE CONDUIT MANUFACTURER'S NAME, CONDUIT SIZE, TYPE AND DATE CODE MUST BE PRINTED ON THE SURFACE OF THE CONDUIT.

-ALL CONDUIT MUST BE 2”

-ALL PVC COUPLINGS MUST HAVE A CENTER STOP.

-BENDS MUST HAVE A 36" MINIMUM RADIUS. ALL BENDS MUST HAVE AN INTEGRAL BELL ON ONE END.

-A DETECTABLE MULE STRING MUST BE INSTALLED IN EACH CONDUIT RUN WITH A TENSILE STRENGTH OF 2500lb.

-WHEN HDPE CONDUIT IS USED, AND A PVC BEND IS NECESSARY IT MUST BE ATTACHED AS DESCRIBED BELOW:

A. SHUR LOCK II COUPLINGS: THESE ARE PLASTIC, SLIP-ON COUPLINGS, WITH STAINLESS STEEL BANDS MADE BY DURALINE.

B. BONDUIT ADHESIVE: THIS ADHESIVE IS FORMULATED TO BOND TO BOTH HDPE AND PVC.

C. MOR CLAMP COUPLINGS: THESE ARE BOLTED, STAINLESS STEEL, SLIP-ON COUPLINGS MADE BY DURALINE. THESE COUPLINGS ARE

EXPENSIVE, SO THEY WILL TYPICALLY BE USED ONLY ON LARGE CONDUIT AND ONLY WHEN NECESSARY BECAUSE THE CONDUIT IS

THESE METHODS ALSO ALLOW HDPE CONDUIT PIECES TO BE JOINED TOGETHER OR FOR HDPE CONDUIT TO BE JOINED TO PVC

CONDUIT AND FITTING INSTALLATION

-REMOVE ANY SHARP EDGES THAT ARE CREATED ON THE INSIDE OR OUTSIDE OF CONDUIT WHEN IT IS CUT.

-CONDUIT MUST LIE FLAT ON THE BOTTOM OF THE TRENCH.

-EXAMINE ALL CONDUIT AND CONDUIT ACCESSORIES BEFORE THEY ARE INSTALLED FOR SHARP EDGES, OUT-OF-ROUND SHAPE, CRACKS,

CHIPS, BURRS, AND INSIDE PROTRUSIONS THAT WOULD DAMAGE THE CABLE WHEN IT IS PULLED INTO POSITION. SUCH PIECES SHALL

NOT BE INSTALLED.

-ALL SECTIONS OF PVC CONDUIT AND ALL FITTINGS MUST BE CEMENTED TOGETHER USING A PVC CONDUIT SOLVENT CEMENT RATED FOR

USE WITH ELECTRICAL PVC CONDUIT THAT CHEMICALLY BONDS THE TWO PVC PARTS TOGETHER. DO NOT USE CEMENT DESIGNED FOR USE

WITH PLUMBING PVC PIPE. THE MATING SURFACES MUST BE 1) PROPERLY CLEANED; 2) A THIN, UNIFORM COATING OF CEMENT APPLIED OVER THE ENTIRE MATING SURFACES (THE OUTER SURFACE OF A PLAIN END AND THE INNER SURFACE OF A BELL END); 3) FULLY SEAT

BOTH PIECES; AND 4) TWIST THE PIECES ONE QUARTER TURN TO THEIR REQUIRED POSITION.

-MULE DETECTABLE TAPE SEGMENTS MUST BE TESTED TO VERIFY THEY WERE NOT INADVERTENTLY GLUED TO A PIECE OF CONDUIT OR A FITTING. THE CUSTOMER WILL BE REQUIRED TO INSTALL NEW DETECTABLE MULE TAPE IN ANY CONDUIT SEGMENT WHERE THE INITIAL DETECTABLE MULE TAPE IS NOT USABLE.

-A CONTINUOUS DETECTABLE MULE TAPE, WITH NO KNOTS OR SPLICES, MUST BE PROVIDED THROUGHOUT THE LENGTH OF EACH INDIVIDUAL

CONDUIT SEGMENT AND EXTEND AT LEAST 18” OUTSIDE OF EACH END.

-CONDUITS MUST BE PLUGGED (PLUG SHALL NOT BE GLUED) TO PREVENT DEBRIS, RAIN, ETC. FROM ENTERING THE CONDUIT. TAPE OR RAGS ARE NOT SUFFICIENT.

-NO WIRES, CABLES, CONDUITS, INNER-DUCTS, OR ANY OTHER ITEMS MAY BE INSTALLED IN THE CONDUITS INSTALLED FOR DUKE

ENERGY. THIS INCLUDES FACILITIES FOR PRIVATE LIGHTING, SECURITY, LANDSCAPING, COMMUNICATION, OTHER UTILITIES OR THE CUSTOMER.

-THE CUSTOMER WILL BE REQUIRED TO REMOVE ANY SUCH FACILITIES THAT ARE FOUND.

-ALL CONDUITS MUST BE FREE OF WATER, MUD, DIRT OR ANY OTHER FOREIGN MATTER. THE CUSTOMER MUST INSPECT, CLEAN AND

REPAIR ANY CONDUITS THAT CONTAIN FOREIGN MATTER.