## Wall-1 RA
[9 empty] | Made by: | AI | Date: | 2025-11-20 | Job No: | 20230339
[9 empty] | Checked by: | TDA | Date: | 2025-12-05 | Sheet No: | 1
[9 empty] | Project: | Bridge ST St_Bowerston |  | PID: | 120494
[9 empty] | Subject: | Temporary Shoring 1 at Rear Abutment
Temporary Shoring 1 at Rear Abutment
Boring Data
Soil Properties Based off of Borring B-002-0-24 | [15 empty] | Layer | Top | Bottom | Depth | Φ | gamma | ka1 | ka2 | Cohesive Strength | E50 | K (py) | typ
[16 empty] | 1 | 943.7 | 940.2 | 3.5 | 24 | 124 | 0.42173 | 0.42173 | 750 | 0.015 | 80 | Stiff Clay W/O Free Water (Reese)
|  |  | Top of Wall Elevation = | 943.477 | ft | [10 empty] | 2 | 940.2 | 935.2 | 8.5 | - | 124 | #VALUE! | #VALUE! | 750 | 0.015 | 80 | Stiff Clay W/O Free Water (Reese)
|  |  | Bottom of Wall Elevation = | 931.28 | ft | [10 empty] | 3 | 935.2 | 932.2 | 11.5 | - | 122 | #VALUE! | #VALUE! | 250 | 0.03 | 15 | Stiff Clay W/O Free Water (Reese)
|  |  | Water Table Elevation = | 935.2 | [11 empty] | 4 | 932.2 | 929.2 | 14.5 | 28 | 110 | 0.36103 | 0.36103 | - | - | 20 | Sand (Reese)
|  |  | H (design)= | 12.197 | ft | [10 empty] | 5 | 929.2 | 924.7 | 19 | 28 | 110 | 0.36103 | 0.36103 | - | - | 20 | Sand (Reese)
|  |  | Su = | 0 | psf | (Conservative) | [9 empty] | 6 | 924.7 | 920.2 | 23.5 | - | 124 | #VALUE! | #VALUE! | 750 | 0.015 | 80 | Stiff Clay W/O Free Water (Reese)
|  |  | Gamma = | 125 | pcf | [10 empty] | 7 | 920.2 | 910.2 | 33.5 | - | 126 | #VALUE! | #VALUE! | 1500 | 0.01 | 350 | Stiff Clay W/O Free Water (Reese)
|  |  | Submerged Gamma = | 145 | pcf
|  |  | Backslope Angle = | 0 | [11 empty] | 8 | 910.2 | 893.7 | 50 | - | 131 | #VALUE! | #VALUE! | 4500 | 0.004 | 1500 | Stiff Clay W/O Free Water (Reese)
|  |  | Piling Spacing S = | 0 | ft
|  |  | ka1 = | 0.42173
|  |  | ka2 = | 0.42173
|  |  | Water Density = | 62.4 | pcf
|  |  | Surcharge Load Equivalent Height = | 2
AASHTO LRFD Load Factors
Reference Tbl. 3.4.1-1 & 3.4.1-2
Limit State |  | EH | LL | WA
Service I |  | 1 | 1 | 1
Strength I |  | 1.5 | 1.75 | 1
Load Pressure Calculations | [14 empty] | y | x
Limit State |  | Depth Below Head (ft) | EH | LL | WA | [9 empty] | 0 | 0
Top of Wall |  | 0 | 0 | 105.4326 | 0 | psf | [8 empty] | 0 | 105.4326
Water Table |  | 8.277 | 436.3326 | 105.4326 | 0 | psf | [8 empty] | 12.197 | 922.9261
Bottom of Wall |  | 12.197 | 572.8855 | 105.4326 | 244.608 | psf | [8 empty] | 12.197 | 0
PYWALL Unfiromly Distributed Load (LL Surcharge) Inputs
Location |  | Service I Min (lbs/in) | Strength I Max (lbs/in)
Top of Wall |  | 250 | 291.6667 | Note: Pywall uses a active earth modification factor, for service case it is 1 but for strength case it is 1.5 and it multiplies surcharge load by 1.5 by default so to get around this in strength case surchage load needs to be multiplied by 1.75/1.5.
Bottom of Wall |  | 250 | 291.6667
SOIL LAYER SETUP FOR PYWALL
No |  | Type |  | Depth at Top of the Layer | Depth at Bottom of Layer | Friction angle Φ | Unit Weight | Cohesive Strength | E50 | K (py) (pci) | Pressure coefficient
1 |  | Stiff Clay W/O Free Water (Reese) |  | -0.223 | 3.277 | 24 | 124 | 750 | 0.015 | 80 | 0.42173 | 0.42173
2 |  | Stiff Clay W/O Free Water (Reese) |  | 3.277 | 8.277 | - | 124 | 750 | 0.015 | 80 | 0.42173 | 0.42173
3 |  | Stiff Clay W/O Free Water (Reese) |  | 8.277 | 11.277 | - | 122 | 250 | 0.03 | 15 | 0.42173 | 0.42173
4 |  | Sand (Reese) |  | 11.277 | 12.197 | - | 122 | 250 | 0.03 | 15 | 0.42173 | 0.42173
5 |  | Sand (Reese) |  | 12.197 | 14.277 | 28 | 110 | - | - | 20
6 |  | Stiff Clay W/O Free Water (Reese) |  | 14.277 | 18.777 | 28 | 110 | - | - | 20
7 |  | Stiff Clay W/O Free Water (Reese) |  | 18.777 | 23.277 | - | 124 | 750 | 0.015 | 80
8 |  | Stiff Clay W/O Free Water (Reese) |  | 23.277 | 33.277 | - | 126 | 1500 | 0.01 | 350
9 |  | Stiff Clay W/O Free Water (Reese) |  | 33.277 | 49.777 | - | 131 | 4500 | 0.004 | 1500
PYWALL results
SHEET PILE
[5 empty] | SECTION = | PZ 40
[5 empty] | Depth = | 40.1 | ft
[5 empty] | Service Level Deflection = | 3.17 | in | < OK | 3.6591 | in | 86.6333
[5 empty] | Strength Level Deflection = | 7.403 | in
[5 empty] | Max Strength I Moment Above Excavation Line = | 58.775 | kip-ft | < OK | 373.4947 | k-ft
[5 empty] | Max Strength I Moment Below Excavation Line = | 227.8333 | kip-ft | < OK | 373.4947 | k-ft
[5 empty] | Max Strength I Shear = | 30.5 | kips | < OK | 127.2524 | kips (LRFD Section 6.10.9.2)
STA I | X | DEFL. | SLOPE | MOMENT | SHEAR | SOIL_REACT | NET_FORCE/STA | EI |  |  | Depth (ft) | Deflection (in) | Moment (in-lbs) | Shear ( lbs) |  | Max Moment above |  |  | Max Shear
| FT | IN | RAD | LBS-IN | LBS | LBS/IN | LBS | LBS-IN**2 |  |  | 0 | 7.403 | 0 | 0 |  | 705300 | lb-in |  | 30500 |  | lbs
------ | ---- | ---- | ----- | ------ | ------ | --------- | --------- | --------- |  |  | 0.401 | 7.279 | 0 | 71.05
0 | 0 | 7.403 | -0.02568 | 0 | 0 | 0 | 0 | 23360000000 |  |  | 0.802 | 7.156 | 683.8 | 223.5
1 | 0.401 | 7.279 | -0.02568 | 0 | 71.05 | 0 | 142.1 | 23360000000 |  |  | 1.203 | 7.032 | 2151 | 396.6 |  | Max Moment below
2 | 0.802 | 7.156 | -0.02568 | 683.8 | 223.5 | 0 | 162.8 | 23360000000 |  |  | 1.604 | 6.909 | 4501 | 590.5 |  | 2734000 | kip-in |  | 0.86633
3 | 1.203 | 7.032 | -0.02568 | 2151 | 396.6 | 0 | 183.5 | 23360000000 |  |  | 2.005 | 6.785 | 7834 | 805
4 | 1.604 | 6.909 | -0.02568 | 4501 | 590.5 | 0 | 204.2 | 23360000000 |  |  | 2.406 | 6.661 | 12250 | 1040
5 | 2.005 | 6.785 | -0.02568 | 7834 | 805 | 0 | 224.9 | 23360000000 |  |  | 2.807 | 6.538 | 17850 | 1296
6 | 2.406 | 6.661 | -0.02568 | 12250 | 1040 | 0 | 245.6 | 23360000000 |  |  | 3.208 | 6.414 | 24720 | 1573
7 | 2.807 | 6.538 | -0.02567 | 17850 | 1296 | 0 | 266.3 | 23360000000 |  |  | 3.609 | 6.291 | 32980 | 1870
8 | 3.208 | 6.414 | -0.02567 | 24720 | 1573 | 0 | 287 | 23360000000 |  |  | 4.01 | 6.167 | 42720 | 2188
9 | 3.609 | 6.291 | -0.02566 | 32980 | 1870 | 0 | 307.7 | 23360000000 |  |  | 4.411 | 6.044 | 54040 | 2527
10 | 4.01 | 6.167 | -0.02565 | 42720 | 2188 | 0 | 328.4 | 23360000000 |  |  | 4.812 | 5.921 | 67040 | 2886
11 | 4.411 | 6.044 | -0.02564 | 54040 | 2527 | 0 | 349.1 | 23360000000 |  |  | 5.213 | 5.797 | 81820 | 3266
12 | 4.812 | 5.921 | -0.02563 | 67040 | 2886 | 0 | 369.8 | 23360000000 |  |  | 5.614 | 5.674 | 98480 | 3667
13 | 5.213 | 5.797 | -0.02562 | 81820 | 3266 | 0 | 390.5 | 23360000000 |  |  | 6.015 | 5.551 | 117100 | 4089
14 | 5.614 | 5.674 | -0.0256 | 98480 | 3667 | 0 | 411.2 | 23360000000 |  |  | 6.416 | 5.428 | 137800 | 4531
15 | 6.015 | 5.551 | -0.02558 | 117100 | 4089 | 0 | 431.9 | 23360000000 |  |  | 6.817 | 5.305 | 160700 | 4994
16 | 6.416 | 5.428 | -0.02555 | 137800 | 4531 | 0 | 452.5 | 23360000000 |  |  | 7.218 | 5.182 | 185900 | 5477
17 | 6.817 | 5.305 | -0.02552 | 160700 | 4994 | 0 | 473.2 | 23360000000 |  |  | 7.619 | 5.06 | 213400 | 5982
18 | 7.218 | 5.182 | -0.02548 | 185900 | 5477 | 0 | 493.9 | 23360000000 |  |  | 8.02 | 4.937 | 243500 | 6507
19 | 7.619 | 5.06 | -0.02544 | 213400 | 5982 | 0 | 514.6 | 23360000000 |  |  | 8.421 | 4.815 | 276100 | 7052
20 | 8.02 | 4.937 | -0.0254 | 243500 | 6507 | 0 | 535.3 | 23360000000 |  |  | 8.822 | 4.694 | 311300 | 7619
21 | 8.421 | 4.815 | -0.02534 | 276100 | 7052 | 0 | 556 | 23360000000 |  |  | 9.223 | 4.572 | 349400 | 8206
22 | 8.822 | 4.694 | -0.02528 | 311300 | 7619 | 0 | 576.7 | 23360000000 |  |  | 9.624 | 4.451 | 390300 | 8816
23 | 9.223 | 4.572 | -0.02521 | 349400 | 8206 | 0 | 597.4 | 23360000000 |  |  | 10.03 | 4.33 | 434200 | 9459
24 | 9.624 | 4.451 | -0.02514 | 390300 | 8816 | 0 | 623.6 | 23360000000 |  |  | 10.43 | 4.21 | 481300 | 10140
25 | 10.03 | 4.33 | -0.02505 | 434200 | 9459 | 0 | 662 | 23360000000 |  |  | 10.83 | 4.09 | 531800 | 10860
26 | 10.43 | 4.21 | -0.02496 | 481300 | 10140 | 0 | 700.4 | 23360000000 |  |  | 11.23 | 3.971 | 585800 | 11620
27 | 10.83 | 4.09 | -0.02485 | 531800 | 10860 | 0 | 738.9 | 23360000000 |  |  | 11.63 | 3.852 | 643600 | 12410
28 | 11.23 | 3.971 | -0.02474 | 585800 | 11620 | 0 | 777.3 | 23360000000 |  |  | 12.03 | 3.734 | 705300 | 13240
29 | 11.63 | 3.852 | -0.02461 | 643600 | 12410 | 0 | 813.6 | 23360000000 |  |  | 12.43 | 3.616 | 771100 | 13980
30 | 12.03 | 3.734 | -0.02447 | 705300 | 13240 | -1.245 | 843.6 | 23360000000 |  |  | 12.83 | 3.5 | 839800 | 14540
31 | 12.43 | 3.616 | -0.02432 | 771100 | 13980 | -29.1 | 624.2 | 23360000000 |  |  | 13.23 | 3.384 | 911000 | 14970
32 | 12.83 | 3.5 | -0.02415 | 839800 | 14540 | -55.74 | 496 | 23360000000 |  |  | 13.63 | 3.269 | 983900 | 15270
33 | 13.23 | 3.384 | -0.02397 | 911000 | 14970 | -82.41 | 367.7 | 23360000000 |  |  | 14.04 | 3.155 | 1058000 | 15500
34 | 13.63 | 3.269 | -0.02378 | 983900 | 15270 | -109.1 | 239.2 | 23360000000 |  |  | 14.44 | 3.042 | 1133000 | 15700
35 | 14.04 | 3.155 | -0.02357 | 1058000 | 15500 | -114.8 | 212 | 23360000000 |  |  | 14.84 | 2.93 | 1209000 | 15870
36 | 14.44 | 3.042 | -0.02334 | 1133000 | 15700 | -120.4 | 184.8 | 23360000000 |  |  | 15.24 | 2.82 | 1286000 | 16010
37 | 14.84 | 2.93 | -0.0231 | 1209000 | 15870 | -126 | 157.6 | 23360000000 |  |  | 15.64 | 2.71 | 1363000 | 16120
38 | 15.24 | 2.82 | -0.02284 | 1286000 | 16010 | -131.7 | 130.5 | 23360000000 |  |  | 16.04 | 2.603 | 1441000 | 16180
39 | 15.64 | 2.71 | -0.02257 | 1363000 | 16120 | -141.2 | 84.86 | 23360000000 |  |  | 16.44 | 2.496 | 1519000 | 16200
40 | 16.04 | 2.603 | -0.02228 | 1441000 | 16180 | -150.7 | 39.26 | 23360000000 |  |  | 16.84 | 2.391 | 1597000 | 16170
41 | 16.44 | 2.496 | -0.02198 | 1519000 | 16200 | -160.1 | -6.329 | 23360000000 |  |  | 17.24 | 2.288 | 1674000 | 16080
42 | 16.84 | 2.391 | -0.02166 | 1597000 | 16170 | -169.6 | -51.92 | 23360000000 |  |  | 17.64 | 2.186 | 1752000 | 15930
43 | 17.24 | 2.288 | -0.02132 | 1674000 | 16080 | -183.4 | -118.3 | 23360000000 |  |  | 18.05 | 2.086 | 1828000 | 15710
44 | 17.64 | 2.186 | -0.02097 | 1752000 | 15930 | -197.2 | -184.7 | 23360000000 |  |  | 18.45 | 1.988 | 1903000 | 15430
45 | 18.05 | 2.086 | -0.0206 | 1828000 | 15710 | -211 | -251.1 | 23360000000 |  |  | 18.85 | 1.891 | 1976000 | 14920
46 | 18.45 | 1.988 | -0.02021 | 1903000 | 15430 | -224.8 | -317.5 | 23360000000 |  |  | 19.25 | 1.797 | 2046000 | 14250
47 | 18.85 | 1.891 | -0.01982 | 1976000 | 14920 | -215.8 | -695.6 | 23360000000 |  |  | 19.65 | 1.705 | 2113000 | 13640
48 | 19.25 | 1.797 | -0.0194 | 2046000 | 14250 | -205.5 | -645.8 | 23360000000 |  |  | 20.05 | 1.614 | 2178000 | 13060
49 | 19.65 | 1.705 | -0.01897 | 2113000 | 13640 | -192.4 | -582.8 | 23360000000 |  |  | 20.45 | 1.526 | 2239000 | 12480
50 | 20.05 | 1.614 | -0.01853 | 2178000 | 13060 | -191.9 | -580.6 | 23360000000 |  |  | 20.85 | 1.44 | 2298000 | 11900
51 | 20.45 | 1.526 | -0.01808 | 2239000 | 12480 | -191.4 | -578.2 | 23360000000 |  |  | 21.25 | 1.357 | 2354000 | 11320
52 | 20.85 | 1.44 | -0.01761 | 2298000 | 11900 | -190.9 | -575.8 | 23360000000 |  |  | 21.65 | 1.275 | 2407000 | 10750
53 | 21.25 | 1.357 | -0.01713 | 2354000 | 11320 | -190.4 | -573.4 | 23360000000 |  |  | 22.06 | 1.197 | 2457000 | 10180
54 | 21.65 | 1.275 | -0.01664 | 2407000 | 10750 | -189.9 | -571.1 | 23360000000 |  |  | 22.46 | 1.12 | 2505000 | 9615
55 | 22.06 | 1.197 | -0.01614 | 2457000 | 10180 | -189.4 | -568.7 | 23360000000 |  |  | 22.86 | 1.046 | 2550000 | 9050
56 | 22.46 | 1.12 | -0.01563 | 2505000 | 9615 | -188.9 | -566.2 | 23360000000 |  |  | 23.26 | 0.9748 | 2592000 | 8316
57 | 22.86 | 1.046 | -0.01511 | 2550000 | 9050 | -188.4 | -563.9 | 23360000000 |  |  | 23.66 | 0.9059 | 2630000 | 7350
58 | 23.26 | 0.9748 | -0.01458 | 2592000 | 8316 | -188 | -904.5 | 23360000000 |  |  | 24.06 | 0.8397 | 2662000 | 6265
59 | 23.66 | 0.9059 | -0.01404 | 2630000 | 7350 | -213.5 | -1027 | 23360000000 |  |  | 24.46 | 0.7761 | 2690000 | 5067
60 | 24.06 | 0.8397 | -0.01349 | 2662000 | 6265 | -237.6 | -1143 | 23360000000 |  |  | 24.86 | 0.7151 | 2711000 | 3762
61 | 24.46 | 0.7761 | -0.01294 | 2690000 | 5067 | -260.4 | -1253 | 23360000000 |  |  | 25.26 | 0.6569 | 2726000 | 2357
62 | 24.86 | 0.7151 | -0.01239 | 2711000 | 3762 | -281.9 | -1357 | 23360000000 |  |  | 25.66 | 0.6013 | 2734000 | 855.5
63 | 25.26 | 0.6569 | -0.01183 | 2726000 | 2357 | -302.2 | -1454 | 23360000000 |  |  | 26.07 | 0.5485 | 2734000 | -685.9
64 | 25.66 | 0.6013 | -0.01126 | 2734000 | 855.5 | -321.9 | -1549 | 23360000000 |  |  | 26.47 | 0.4984 | 2727000 | -2213
65 | 26.07 | 0.5485 | -0.0107 | 2734000 | -685.9 | -318.8 | -1534 | 23360000000 |  |  | 26.87 | 0.4509 | 2713000 | -3721
66 | 26.47 | 0.4984 | -0.01014 | 2727000 | -2213 | -315.9 | -1520 | 23360000000 |  |  | 27.27 | 0.4062 | 2692000 | -5205
67 | 26.87 | 0.4509 | -0.009576 | 2713000 | -3721 | -311.1 | -1497 | 23360000000 |  |  | 27.67 | 0.3641 | 2663000 | -6662
68 | 27.27 | 0.4062 | -0.00902 | 2692000 | -5205 | -305.5 | -1470 | 23360000000 |  |  | 28.07 | 0.3247 | 2627000 | -8090
69 | 27.67 | 0.3641 | -0.008468 | 2663000 | -6662 | -300.2 | -1445 | 23360000000 |  |  | 28.47 | 0.2879 | 2585000 | -9486
70 | 28.07 | 0.3247 | -0.007923 | 2627000 | -8090 | -293.3 | -1412 | 23360000000 |  |  | 28.87 | 0.2536 | 2536000 | -10850
71 | 28.47 | 0.2879 | -0.007386 | 2585000 | -9486 | -286.7 | -1380 | 23360000000 |  |  | 29.27 | 0.2219 | 2481000 | -12180
72 | 28.87 | 0.2536 | -0.006859 | 2536000 | -10850 | -280.6 | -1350 | 23360000000 |  |  | 29.67 | 0.1926 | 2419000 | -13470
73 | 29.27 | 0.2219 | -0.006342 | 2481000 | -12180 | -272.8 | -1313 | 23360000000 |  |  | 30.08 | 0.1657 | 2351000 | -14730
74 | 29.67 | 0.1926 | -0.005837 | 2419000 | -13470 | -264 | -1270 | 23360000000 |  |  | 30.48 | 0.1411 | 2277000 | -15940
75 | 30.08 | 0.1657 | -0.005346 | 2351000 | -14730 | -256 | -1232 | 23360000000 |  |  | 30.88 | 0.1188 | 2198000 | -17120
76 | 30.48 | 0.1411 | -0.004869 | 2277000 | -15940 | -248.6 | -1196 | 23360000000 |  |  | 31.28 | 0.09871 | 2112000 | -18250
77 | 30.88 | 0.1188 | -0.004408 | 2198000 | -17120 | -241.7 | -1163 | 23360000000 |  |  | 31.68 | 0.08068 | 2022000 | -19330
78 | 31.28 | 0.09871 | -0.003964 | 2112000 | -18250 | -229.6 | -1105 | 23360000000 |  |  | 32.08 | 0.06466 | 1926000 | -20360
79 | 31.68 | 0.08068 | -0.003538 | 2022000 | -19330 | -218.7 | -1053 | 23360000000 |  |  | 32.48 | 0.05054 | 1826000 | -21350
80 | 32.08 | 0.06466 | -0.003132 | 1926000 | -20360 | -209.1 | -1006 | 23360000000 |  |  | 32.88 | 0.03824 | 1721000 | -22280
81 | 32.48 | 0.05054 | -0.002745 | 1826000 | -21350 | -200.6 | -965.4 | 23360000000 |  |  | 33.28 | 0.02764 | 1612000 | -23920
82 | 32.88 | 0.03824 | -0.00238 | 1721000 | -22280 | -187.3 | -901.4 | 23360000000 |  |  | 33.68 | 0.01864 | 1491000 | -26210
83 | 33.28 | 0.02764 | -0.002036 | 1612000 | -23920 | -494.5 | -2379 | 23360000000 |  |  | 34.09 | 0.01112 | 1359000 | -28280
84 | 33.68 | 0.01864 | -0.001717 | 1491000 | -26210 | -457.3 | -2201 | 23360000000 |  |  | 34.49 | 0.00494 | 1219000 | -29990
85 | 34.09 | 0.01112 | -0.001423 | 1359000 | -28280 | -401.4 | -1931 | 23360000000 |  |  | 34.89 | -2.685e-05 | 1071000 | -30500
86 | 34.49 | 0.00494 | -0.001158 | 1219000 | -29990 | -312.7 | -1505 | 23360000000 |  |  | 35.29 | -0.003933 | 925000 | -29430
87 | 34.89 | -2.685e-05 | -0.0009219 | 1071000 | -30500 | 100.7 | 484.7 | 23360000000 |  |  | 35.69 | -0.006921 | 787300 | -27640
88 | 35.29 | -0.003933 | -0.0007164 | 925000 | -29430 | 343.9 | 1655 | 23360000000 |  |  | 36.09 | -0.009129 | 659000 | -25590
89 | 35.69 | -0.006921 | -0.00054 | 787300 | -27640 | 403.7 | 1943 | 23360000000 |  |  | 36.49 | -0.01068 | 541100 | -23380
90 | 36.09 | -0.009129 | -0.000391 | 659000 | -25590 | 448.4 | 2158 | 23360000000 |  |  | 36.89 | -0.0117 | 434000 | -21100
91 | 36.49 | -0.01068 | -0.0002674 | 541100 | -23380 | 468.7 | 2256 | 23360000000 |  |  | 37.29 | -0.01229 | 338000 | -18780
92 | 36.89 | -0.0117 | -0.0001669 | 434000 | -21100 | 479.3 | 2306 | 23360000000 |  |  | 37.69 | -0.01254 | 253300 | -16430
93 | 37.29 | -0.01229 | -8.74e-05 | 338000 | -18780 | 485.9 | 2338 | 23360000000 |  |  | 38.1 | -0.01255 | 179900 | -14070
94 | 37.69 | -0.01254 | -2.648e-05 | 253300 | -16430 | 489.5 | 2356 | 23360000000 |  |  | 38.5 | -0.01237 | 117900 | -11710
95 | 38.1 | -0.01255 | 1.815e-05 | 179900 | -14070 | 490.9 | 2362 | 23360000000 |  |  | 38.9 | -0.01208 | 67240 | -8763
96 | 38.5 | -0.01237 | 4.883e-05 | 117900 | -11710 | 490.6 | 2361 | 23360000000 |  |  | 39.3 | -0.01172 | 33560 | -5826
97 | 38.9 | -0.01208 | 6.79e-05 | 67240 | -8763 | 733.8 | 3531 | 23360000000 |  |  | 39.7 | -0.01132 | 11170 | -3487
98 | 39.3 | -0.01172 | 7.828e-05 | 33560 | -5826 | 487.1 | 2344 | 23360000000 |  |  | 40.1 | -0.01092 | -1.75e-09 | -1160
99 | 39.7 | -0.01132 | 8.289e-05 | 11170 | -3487 | 484.8 | 2333 | 23360000000
100 | 40.1 | -0.01092 | 8.404e-05 | -1.75e-09 | -1160 | 482.3 | 2321 | 23360000000
Note on E16: tadams: We need add this to the model for the total unit weight below the water table.
Note on E19: tadams: Enter these into the soil properties in PYWall
Note on G58: tadams: I created a separate model for the strength case. PYWall was applying the 1.5 load factor to the water load, which shouldn't have a load factor at all. I modified the elevation of the water table to match the loading at the base of wall for the service case.
Note on A67: aibrahimkhail: results from Pywall

## Wall-2 SW WW
[9 empty] | Made by: | AI | Date: | 2025-11-20 | Job No: | 20230339
[9 empty] | Checked by: | TDA | Date: | 2025-12-05 | Sheet No: | 1
[9 empty] | Project: | Bridge ST St_Bowerston |  | PID: | 120494
[9 empty] | Subject: | Temporary Shoring 2 at Southwest Wingwall
Temporary Shoring 2 at Southwest Wingwall
Boring Data
Soil Properties Based off of Borring B-002-0-24 | [15 empty] | Layer | Top | Bottom | Depth | Φ | gamma | ka1 | ka2 | Cohesive Strength | E50 | K (py) | typ
[16 empty] | 1 | 943.7 | 940.2 | 3.5 | 24 | 124 | 0.42173 | 0.42173 | 750 | 0.015 | 80 | Stiff Clay W/O Free Water (Reese)
|  |  | Top of Wall Elevation = | 942.81 | ft | [10 empty] | 2 | 940.2 | 935.2 | 8.5 | - | 124 | #VALUE! | #VALUE! | 750 | 0.015 | 80 | Stiff Clay W/O Free Water (Reese)
|  |  | Bottom of Wall Elevation = | 931.28 | ft | 7.61 | [9 empty] | 3 | 935.2 | 932.2 | 11.5 | - | 122 | #VALUE! | #VALUE! | 250 | 0.03 | 15 | Stiff Clay W/O Free Water (Reese)
|  |  | Water Table Elevation = | 935.2 |  |  |  | ee | [7 empty] | 4 | 932.2 | 929.2 | 14.5 | 28 | 110 | 0.36103 | 0.36103 | - | - | 20 | Sand (Reese)
|  |  | H (design)= | 11.53 | ft | [10 empty] | 5 | 929.2 | 924.7 | 19 | 28 | 110 | 0.36103 | 0.36103 | - | - | 20 | Sand (Reese)
|  |  | Su = | 0 | psf | (Conservative) | [9 empty] | 6 | 924.7 | 920.2 | 23.5 | - | 124 | #VALUE! | #VALUE! | 750 | 0.015 | 80 | Stiff Clay W/O Free Water (Reese)
|  |  | Gamma = | 124 | pcf | [10 empty] | 7 | 920.2 | 910.2 | 33.5 | - | 126 | #VALUE! | #VALUE! | 1500 | 0.01 | 350 | Stiff Clay W/O Free Water (Reese)
|  |  | Saturated Gamma = | 145 | pcf
|  |  | Backslope Angle = | 0 | [11 empty] | 8 | 910.2 | 893.7 | 50 | - | 131 | #VALUE! | #VALUE! | 4500 | 0.004 | 1500 | Stiff Clay W/O Free Water (Reese)
|  |  | Sheet Pile Width = | 1.6408 | ft
|  |  | ka1 = | 0.42173
|  |  | ka2 = | 0.42173
|  |  | Water Density = | 62.4 | pcf
|  |  | Surcharge Load Equivalent Height = | 0
AASHTO LRFD Load Factors
Reference Tbl. 3.4.1-1 & 3.4.1-2
Limit State |  | EH | LL | WA
Service I |  | 1 | 1 | 1 | [17 empty] | Shoring design - The "maximum retained height" from the plans (12.0', 11.53', 12.0') exceeds the design height in the shorting calculations (9.64', 10.72', 9.49').
Strength I |  | 1.5 | 1.75 | 1
Load Pressure Calculations | [14 empty] | y | x
Limit State |  | Depth Below Head (ft) | EH | LL | WA | [9 empty] | 0 | 0 | 942.81
Top of Wall |  | 0 | 0 | 0 | 0 | psf | [8 empty] | 0 | 0 | 942.81
Water Table |  | 7.61 | 397.9615 | 0 | 0 | psf | [8 empty] | 11.53 | 779.1224 | 954.34
Bottom of Wall |  | 11.53 | 534.5144 | 0 | 244.608 | psf | [8 empty] | 11.53 | 0 | 954.34
PYWALL Unfiromly Distributed Load (LL Surcharge) Inputs
Location |  | Service I Min (lbs/in) | Strength I Max (lbs/in)
Top of Wall |  | 0 | 0 | Note: Pywall uses a active earth modification factor, for service case it is 1 but for strength case it is 1.5 and it multiplies surcharge load by 1.5 by default so to get around this in strength case surchage load needs to be multiplied by 1.75/1.5.
Bottom of Wall |  | 0 | 0
SOIL LAYER SETUP FOR PYWALL
No |  | Type |  | Depth at Top of the Layer | Depth at Bottom of Layer | Friction angle Φ | Unit Weight | Cohesive Strength | E50 | K (py) (pci) | Pressure coefficient
1 |  | Stiff Clay W/O Free Water (Reese) |  | -0.89 | 2.61 | 24 | 124 | 750 | 0.015 | 80 | 0.42173 | 0.42173
2 |  | Stiff Clay W/O Free Water (Reese) |  | 2.61 | 7.61 | - | 124 | 750 | 0.015 | 80 | 0.42173 | 0.42173
3 |  | Stiff Clay W/O Free Water (Reese) |  | 7.61 | 10.61 | - | 122 | 250 | 0.03 | 15 | 0.42173 | 0.42173
4 |  | Sand (Reese) |  | 10.61 | 11.53 | 28 | 110 | - | - | 20 | 0.42173 | 0.42173
5 |  | Sand (Reese) |  | 11.53 | 13.61 | 28 | 110 | - | - | 20
6 |  | Sand (Reese) |  | 13.61 | 18.11 | 28 | 110 | - | - | 20
7 |  | Stiff Clay W/O Free Water (Reese) |  | 18.11 | 22.61 | - | 124 | 750 | 0.015 | 80
8 |  | Stiff Clay W/O Free Water (Reese) |  | 22.61 | 32.61 | - | 126 | 1500 | 0.01 | 350
9 |  | Stiff Clay W/O Free Water (Reese) |  | 32.61 | 49.11 | - | 131 | 4500 | 0.004 | 1500
10
PYWALL results
SHEET PILE
[5 empty] | SECTION = | PZ 40
[5 empty] | Depth = | 40 | ft
[5 empty] | Service Level Deflection = | 1.52 | in | < OK | 2.7672 | "
[5 empty] | Strength Level Deflection = | 3.514 | in
[5 empty] | Max Strength I Moment Above Excavation Line = | 30.9417 | kip-ft | < OK | 373.4947 | k-ft
[5 empty] | Max Strength I Moment Below Excavation Line = | 133 | kip-ft | < OK | 373.4947 | k-ft
[5 empty] | Max Strength I Shear = | 17.2 | kips | < OK | 127.2524 | kips (LRFD Section 6.10.9.2)
STA I | X | DEFL. | SLOPE | MOMENT | SHEAR | SOIL_REACT | NET_FORCE/STA | EI |  |  | Depth (ft) | Deflection (in) | Moment (in-lbs) | Shear ( lbs) |  | Max Moment above |  |  | Max Shear
| FT | IN | RAD | LBS-IN | LBS | LBS/IN | LBS | LBS-IN**2 |  |  | 0 | 3.514 | 0 | 0 |  | 371300 | lb-in |  | 17200 |  | lbs
------ | ---- | ---- | ----- | ------ | ------ | --------- | --------- | --------- |  |  | 0.4 | 3.45 | 0 | 10.3
0 | 0 | 3.514 | -0.0133 | 0 | 0 | 0 | 0 | 23360000000 |  |  | 0.8 | 3.386 | 98.85 | 41.19
1 | 0.4 | 3.45 | -0.0133 | 0 | 10.3 | 0 | 20.59 | 23360000000 |  |  | 1.2 | 3.323 | 395.4 | 92.67 |  | Max Moment below
2 | 0.8 | 3.386 | -0.0133 | 98.85 | 41.19 | 0 | 41.19 | 23360000000 |  |  | 1.6 | 3.259 | 988.5 | 164.7 |  | 1596000 | kip-in
3 | 1.2 | 3.323 | -0.0133 | 395.4 | 92.67 | 0 | 61.78 | 23360000000 |  |  | 2 | 3.195 | 1977 | 257.4
4 | 1.6 | 3.259 | -0.0133 | 988.5 | 164.7 | 0 | 82.37 | 23360000000 |  |  | 2.4 | 3.131 | 3460 | 370.7
5 | 2 | 3.195 | -0.0133 | 1977 | 257.4 | 0 | 103 | 23360000000 |  |  | 2.8 | 3.067 | 5536 | 504.5 |  |  |  | 0.54929
6 | 2.4 | 3.131 | -0.0133 | 3460 | 370.7 | 0 | 123.6 | 23360000000 |  |  | 3.2 | 3.003 | 8303 | 659 |  |  |  | #DIV/0!
7 | 2.8 | 3.067 | -0.0133 | 5536 | 504.5 | 0 | 144.2 | 23360000000 |  |  | 3.6 | 2.94 | 11860 | 834
8 | 3.2 | 3.003 | -0.0133 | 8303 | 659 | 0 | 164.8 | 23360000000 |  |  | 4 | 2.876 | 16310 | 1030
9 | 3.6 | 2.94 | -0.0133 | 11860 | 834 | 0 | 185.3 | 23360000000 |  |  | 4.4 | 2.812 | 21750 | 1246
10 | 4 | 2.876 | -0.01329 | 16310 | 1030 | 0 | 205.9 | 23360000000 |  |  | 4.8 | 2.748 | 28270 | 1483
11 | 4.4 | 2.812 | -0.01329 | 21750 | 1246 | 0 | 226.5 | 23360000000 |  |  | 5.2 | 2.684 | 35980 | 1740
12 | 4.8 | 2.748 | -0.01329 | 28270 | 1483 | 0 | 247.1 | 23360000000 |  |  | 5.6 | 2.621 | 44980 | 2018
13 | 5.2 | 2.684 | -0.01328 | 35980 | 1740 | 0 | 267.7 | 23360000000 |  |  | 6 | 2.557 | 55360 | 2317
14 | 5.6 | 2.621 | -0.01327 | 44980 | 2018 | 0 | 288.3 | 23360000000 |  |  | 6.4 | 2.493 | 67220 | 2636
15 | 6 | 2.557 | -0.01326 | 55360 | 2317 | 0 | 308.9 | 23360000000 |  |  | 6.8 | 2.43 | 80660 | 2976
16 | 6.4 | 2.493 | -0.01325 | 67220 | 2636 | 0 | 329.5 | 23360000000 |  |  | 7.2 | 2.366 | 95780 | 3336
17 | 6.8 | 2.43 | -0.01323 | 80660 | 2976 | 0 | 350.1 | 23360000000 |  |  | 7.6 | 2.303 | 112700 | 3717
18 | 7.2 | 2.366 | -0.01321 | 95780 | 3336 | 0 | 370.7 | 23360000000 |  |  | 8 | 2.24 | 131500 | 4127
19 | 7.6 | 2.303 | -0.01319 | 112700 | 3717 | 0 | 391.3 | 23360000000 |  |  | 8.4 | 2.177 | 152300 | 4576
20 | 8 | 2.24 | -0.01317 | 131500 | 4127 | 0 | 429.1 | 23360000000 |  |  | 8.8 | 2.114 | 175400 | 5062
21 | 8.4 | 2.177 | -0.01314 | 152300 | 4576 | 0 | 467.3 | 23360000000 |  |  | 9.2 | 2.051 | 200900 | 5587
22 | 8.8 | 2.114 | -0.0131 | 175400 | 5062 | 0 | 505.6 | 23360000000 |  |  | 9.6 | 1.988 | 229000 | 6150
23 | 9.2 | 2.051 | -0.01307 | 200900 | 5587 | 0 | 543.8 | 23360000000 |  |  | 10 | 1.926 | 259900 | 6751
24 | 9.6 | 1.988 | -0.01302 | 229000 | 6150 | 0 | 582.1 | 23360000000 |  |  | 10.4 | 1.864 | 293800 | 7390
25 | 10 | 1.926 | -0.01297 | 259900 | 6751 | 0 | 620.3 | 23360000000 |  |  | 10.8 | 1.802 | 330900 | 8067
26 | 10.4 | 1.864 | -0.01291 | 293800 | 7390 | 0 | 658.6 | 23360000000 |  |  | 11.2 | 1.74 | 371300 | 8781
27 | 10.8 | 1.802 | -0.01285 | 330900 | 8067 | 0 | 695.6 | 23360000000 |  |  | 11.6 | 1.679 | 415200 | 9494
28 | 11.2 | 1.74 | -0.01278 | 371300 | 8781 | 0 | 731.4 | 23360000000 |  |  | 12 | 1.618 | 462400 | 10110
29 | 11.6 | 1.679 | -0.0127 | 415200 | 9494 | -0.7477 | 694.3 | 23360000000 |  |  | 12.4 | 1.558 | 512300 | 10600
30 | 12 | 1.618 | -0.01261 | 462400 | 10110 | -28.77 | 547.8 | 23360000000 |  |  | 12.8 | 1.498 | 564200 | 10950
31 | 12.4 | 1.558 | -0.01251 | 512300 | 10600 | -56.07 | 416.8 | 23360000000 |  |  | 13.2 | 1.439 | 617400 | 11170
32 | 12.8 | 1.498 | -0.0124 | 564200 | 10950 | -83.38 | 285.7 | 23360000000 |  |  | 13.6 | 1.38 | 671400 | 11310
33 | 13.2 | 1.439 | -0.01228 | 617400 | 11170 | -110.7 | 154.6 | 23360000000 |  |  | 14 | 1.322 | 726000 | 11420
34 | 13.6 | 1.38 | -0.01214 | 671400 | 11310 | -116.5 | 127 | 23360000000 |  |  | 14.4 | 1.265 | 781000 | 11510
35 | 14 | 1.322 | -0.012 | 726000 | 11420 | -122.2 | 99.37 | 23360000000 |  |  | 14.8 | 1.209 | 836400 | 11570
36 | 14.4 | 1.265 | -0.01184 | 781000 | 11510 | -127.9 | 71.77 | 23360000000 |  |  | 15.2 | 1.153 | 892100 | 11590
37 | 14.8 | 1.209 | -0.01168 | 836400 | 11570 | -133.7 | 44.17 | 23360000000 |  |  | 15.6 | 1.098 | 947700 | 11560
38 | 15.2 | 1.153 | -0.0115 | 892100 | 11590 | -143.9 | -4.67 | 23360000000 |  |  | 16 | 1.045 | 1003000 | 11480
39 | 15.6 | 1.098 | -0.01131 | 947700 | 11560 | -154 | -53.51 | 23360000000 |  |  | 16.4 | 0.9917 | 1058000 | 11350
40 | 16 | 1.045 | -0.01111 | 1003000 | 11480 | -164.2 | -102.3 | 23360000000 |  |  | 16.8 | 0.9399 | 1112000 | 11170
41 | 16.4 | 0.9917 | -0.0109 | 1058000 | 11350 | -174.4 | -151.2 | 23360000000 |  |  | 17.2 | 0.8892 | 1165000 | 10910
42 | 16.8 | 0.9399 | -0.01068 | 1112000 | 11170 | -188.8 | -220.2 | 23360000000 |  |  | 17.6 | 0.8396 | 1217000 | 10590
43 | 17.2 | 0.8892 | -0.01044 | 1165000 | 10910 | -203.1 | -289.2 | 23360000000 |  |  | 18 | 0.7913 | 1267000 | 10200
44 | 17.6 | 0.8396 | -0.0102 | 1217000 | 10590 | -217.5 | -358.2 | 23360000000 |  |  | 18.4 | 0.7442 | 1315000 | 9484
45 | 18 | 0.7913 | -0.009943 | 1267000 | 10200 | -231.9 | -427.2 | 23360000000 |  |  | 18.8 | 0.6984 | 1358000 | 8553
46 | 18.4 | 0.7442 | -0.009677 | 1315000 | 9484 | -207.2 | -994.4 | 23360000000 |  |  | 19.2 | 0.6539 | 1397000 | 7752
47 | 18.8 | 0.6984 | -0.009403 | 1358000 | 8553 | -181 | -868.6 | 23360000000 |  |  | 19.6 | 0.6108 | 1432000 | 7019
48 | 19.2 | 0.6539 | -0.00912 | 1397000 | 7752 | -152.8 | -733.4 | 23360000000 |  |  | 20 | 0.5692 | 1464000 | 6288
49 | 19.6 | 0.6108 | -0.008829 | 1432000 | 7019 | -152.5 | -731.9 | 23360000000 |  |  | 20.4 | 0.5289 | 1493000 | 5559
50 | 20 | 0.5692 | -0.008531 | 1464000 | 6288 | -152.2 | -730.5 | 23360000000 |  |  | 20.8 | 0.4902 | 1517000 | 4833
51 | 20.4 | 0.5289 | -0.008228 | 1493000 | 5559 | -151.7 | -728.1 | 23360000000 |  |  | 21.2 | 0.4529 | 1539000 | 4112
52 | 20.8 | 0.4902 | -0.007918 | 1517000 | 4833 | -150.7 | -723.2 | 23360000000 |  |  | 21.6 | 0.4172 | 1557000 | 3396
53 | 21.2 | 0.4529 | -0.007604 | 1539000 | 4112 | -149.7 | -718.5 | 23360000000 |  |  | 22 | 0.383 | 1572000 | 2684
54 | 21.6 | 0.4172 | -0.007286 | 1557000 | 3396 | -148.8 | -714 | 23360000000 |  |  | 22.4 | 0.3503 | 1583000 | 1977
55 | 22 | 0.383 | -0.006965 | 1572000 | 2684 | -147.9 | -709.8 | 23360000000 |  |  | 22.8 | 0.3192 | 1591000 | 1278
56 | 22.4 | 0.3503 | -0.006641 | 1583000 | 1977 | -146.6 | -703.8 | 23360000000 |  |  | 23.2 | 0.2897 | 1595000 | 541.7
57 | 22.8 | 0.3192 | -0.006314 | 1591000 | 1278 | -144.5 | -693.5 | 23360000000 |  |  | 23.6 | 0.2617 | 1596000 | -279.4
58 | 23.2 | 0.2897 | -0.005987 | 1595000 | 541.7 | -162.4 | -779.7 | 23360000000 |  |  | 24 | 0.2354 | 1592000 | -1181
59 | 23.6 | 0.2617 | -0.005659 | 1596000 | -279.4 | -179.7 | -862.5 | 23360000000 |  |  | 24.4 | 0.2106 | 1584000 | -2156
60 | 24 | 0.2354 | -0.005332 | 1592000 | -1181 | -196 | -940.9 | 23360000000 |  |  | 24.8 | 0.1873 | 1572000 | -3195
61 | 24.4 | 0.2106 | -0.005005 | 1584000 | -2156 | -210.1 | -1009 | 23360000000 |  |  | 25.2 | 0.1656 | 1554000 | -4293
62 | 24.8 | 0.1873 | -0.004681 | 1572000 | -3195 | -222.9 | -1070 | 23360000000 |  |  | 25.6 | 0.1455 | 1530000 | -5408
63 | 25.2 | 0.1656 | -0.00436 | 1554000 | -4293 | -234.6 | -1126 | 23360000000 |  |  | 26 | 0.1268 | 1502000 | -6499
64 | 25.6 | 0.1455 | -0.004043 | 1530000 | -5408 | -229.6 | -1102 | 23360000000 |  |  | 26.4 | 0.1096 | 1468000 | -7562
65 | 26 | 0.1268 | -0.003731 | 1502000 | -6499 | -225 | -1080 | 23360000000 |  |  | 26.8 | 0.09392 | 1429000 | -8588
66 | 26.4 | 0.1096 | -0.003426 | 1468000 | -7562 | -217.9 | -1046 | 23360000000 |  |  | 27.2 | 0.07961 | 1386000 | -9576
67 | 26.8 | 0.09392 | -0.003129 | 1429000 | -8588 | -209.6 | -1006 | 23360000000 |  |  | 27.6 | 0.06666 | 1337000 | -10530
68 | 27.2 | 0.07961 | -0.002839 | 1386000 | -9576 | -202 | -969.7 | 23360000000 |  |  | 28 | 0.05504 | 1284000 | -11450
69 | 27.6 | 0.06666 | -0.00256 | 1337000 | -10530 | -195.2 | -937 | 23360000000 |  |  | 28.4 | 0.04468 | 1227000 | -12340
70 | 28 | 0.05504 | -0.00229 | 1284000 | -11450 | -189.1 | -907.9 | 23360000000 |  |  | 28.8 | 0.03553 | 1166000 | -13190
71 | 28.4 | 0.04468 | -0.002032 | 1227000 | -12340 | -181.9 | -873.1 | 23360000000 |  |  | 29.2 | 0.02753 | 1101000 | -14000
72 | 28.8 | 0.03553 | -0.001786 | 1166000 | -13190 | -172 | -825.6 | 23360000000 |  |  | 29.6 | 0.02062 | 1032000 | -14750
73 | 29.2 | 0.02753 | -0.001553 | 1101000 | -14000 | -163.3 | -784 | 23360000000 |  |  | 30 | 0.01473 | 959100 | -15440
74 | 29.6 | 0.02062 | -0.001334 | 1032000 | -14750 | -150.8 | -723.9 | 23360000000 |  |  | 30.4 | 0.009777 | 883400 | -16060
75 | 30 | 0.01473 | -0.00113 | 959100 | -15440 | -135.6 | -650.9 | 23360000000 |  |  | 30.8 | 0.0057 | 804900 | -16620
76 | 30.4 | 0.009777 | -0.0009402 | 883400 | -16060 | -122.6 | -588.7 | 23360000000 |  |  | 31.2 | 0.002417 | 723900 | -17110
77 | 30.8 | 0.0057 | -0.0007667 | 804900 | -16620 | -112 | -537.4 | 23360000000 |  |  | 31.6 | -0.0001525 | 640700 | -17200
78 | 31.2 | 0.002417 | -0.0006096 | 723900 | -17110 | -92.71 | -445 | 23360000000 |  |  | 32 | -0.00209 | 558800 | -16790
79 | 31.6 | -0.0001525 | -0.0004694 | 640700 | -17200 | 56.72 | 272.3 | 23360000000 |  |  | 32.4 | -0.003475 | 479500 | -16210
80 | 32 | -0.00209 | -0.0003461 | 558800 | -16790 | 113 | 542.4 | 23360000000 |  |  | 32.8 | -0.004388 | 403200 | -15560
81 | 32.4 | -0.003475 | -0.0002395 | 479500 | -16210 | 130.2 | 625 | 23360000000 |  |  | 33.2 | -0.004904 | 330100 | -14780
82 | 32.8 | -0.004388 | -0.0001488 | 403200 | -15560 | 139.6 | 669.9 | 23360000000 |  |  | 33.6 | -0.005093 | 261300 | -13790
83 | 33.2 | -0.004904 | -7.341e-05 | 330100 | -14780 | 185.1 | 888.5 | 23360000000 |  |  | 34 | -0.005025 | 197700 | -12590
84 | 33.6 | -0.005093 | -1.264e-05 | 261300 | -13790 | 228.2 | 1095 | 23360000000 |  |  | 34.4 | -0.004762 | 140400 | -11210
85 | 34 | -0.005025 | 3.453e-05 | 197700 | -12590 | 269.1 | 1292 | 23360000000 |  |  | 34.8 | -0.00436 | 90100 | -9663
86 | 34.4 | -0.004762 | 6.928e-05 | 140400 | -11210 | 306.5 | 1471 | 23360000000 |  |  | 35.2 | -0.003869 | 47630 | -8052
87 | 34.8 | -0.00436 | 9.296e-05 | 90100 | -9663 | 339.7 | 1631 | 23360000000 |  |  | 35.6 | -0.003331 | 12800 | -6484
88 | 35.2 | -0.003869 | 0.0001071 | 47630 | -8052 | 331.3 | 1590 | 23360000000 |  |  | 36 | -0.002781 | -14610 | -4962
89 | 35.6 | -0.003331 | 0.0001133 | 12800 | -6484 | 322 | 1546 | 23360000000 |  |  | 36.4 | -0.002245 | -34830 | -3485
90 | 36 | -0.002781 | 0.0001131 | -14610 | -4962 | 312.4 | 1500 | 23360000000 |  |  | 36.8 | -0.001744 | -48070 | -2064
91 | 36.4 | -0.002245 | 0.0001081 | -34830 | -3485 | 303 | 1454 | 23360000000 |  |  | 37.2 | -0.00129 | -54640 | -729
92 | 36.8 | -0.001744 | 9.954e-05 | -48070 | -2064 | 288.9 | 1387 | 23360000000 |  |  | 37.6 | -0.0008896 | -55070 | 498.1
93 | 37.2 | -0.00129 | 8.898e-05 | -54640 | -729 | 267.3 | 1283 | 23360000000 |  |  | 38 | -0.0005438 | -49860 | 1581
94 | 37.6 | -0.0008896 | 7.771e-05 | -55070 | 498.1 | 244.1 | 1171 | 23360000000 |  |  | 38.4 | -0.0002471 | -39890 | 2498
95 | 38 | -0.0005438 | 6.693e-05 | -49860 | 1581 | 207.1 | 993.9 | 23360000000 |  |  | 38.8 | 1.021e-05 | -25880 | 2755
96 | 38.4 | -0.0002471 | 5.771e-05 | -39890 | 2498 | 175.3 | 841.2 | 23360000000 |  |  | 39.2 | 0.000242 | -13450 | 2212
97 | 38.8 | 1.021e-05 | 5.095e-05 | -25880 | 2755 | -62.06 | -328.3 | 23360000000 |  |  | 39.6 | 0.0004605 | -4649 | 1401
98 | 39.2 | 0.000242 | 4.691e-05 | -13450 | 2212 | -157.8 | -757.9 | 23360000000 |  |  | 40 | 0.0006745 | 0 | 484.3
99 | 39.6 | 0.0004605 | 4.505e-05 | -4649 | 1401 | -179.9 | -864 | 23360000000
100 | 40 | 0.0006745 | 4.457e-05 | 0 | 484.3 | -201.7 | -968.6 | 23360000000
Note on E19: tadams: Enter these into the soil properties in PYWall
Note on A68: aibrahimkhail: results from Pywall

## Wall-3 FA
[9 empty] | Made by: | AI | Date: | 2025-11-20 | Job No: | 20230339
[9 empty] | Checked by: | TDA | Date: | 2025-12-05 | Sheet No: | 1
[9 empty] | Project: | Bridge ST St_Bowerston |  | PID: | 120494
[9 empty] | Subject: | Temporary Shoring 3 at FWD Abutment
Temporary Shoring 3 at FWD Abutment
Boring Data
Soil Properties Based off of Borring B-001-0-24 | [15 empty] | Layer | Top | Bottom | Depth | Φ | gamma | ka1 | ka2 | Cohesive Strength | K (py) | E50 | typ
[16 empty] | 1 | 939.8 | 933.8 | 6 | 24 | 124 | 0.42173 | 0.42173 | 750 | 80 | 0.015 | Stiff Clay W/O Free Water (Reese)
|  |  | Top of Wall Elevation = | 939.987 | ft | [10 empty] | 2 | 933.8 | 928.3 | 11.5 | 28 | 110 | 0.36103 | 0.36103 | - | 25 | - | Sand (Reese)
|  |  | Bottom of Wall Elevation = | 928 | ft | [10 empty] | 3 | 928.3 | 923.8 | 16 | 28 | 110 | 0.36103 | 0.36103 | - | 25 | - | Sand (Reese)
|  |  | Water Table Elevation = | 923.8 | [11 empty] | 4 | 923.8 | 919.3 | 20.5 | 30 | 115 | 0.33333 | 0.33333 | - | 50 | - | Sand (Reese)
|  |  | H (design)= | 11.987 | ft | [10 empty] | 5 | 919.3 | 916.3 | 23.5 | 35 | 127 | 0.27099 | 0.27099 | - | 90 | - | Sand (Reese)
|  |  | Su = |  | psf | (Conservative) | [9 empty] | 6 | 916.3 | 906.3 | 33.5 | - | 126 | #VALUE! | #VALUE! | 1500 | 350 | 0.01 | Stiff Clay With Free Water (Reese)
|  |  | Gamma = | 125 | pcf | [10 empty] | 7 | 906.3 | 901.3 | 38.5 | - | 131 | #VALUE! | #VALUE! | 4500 | 1500 | 0.004 | Stiff Clay With Free Water (Reese)
|  |  | Backslope Angle = | 0
|  |  | Piling Spacing S = | 0 | ft
|  |  | ka1 = | 0.42173
|  |  | ka2 = | 0.42173
|  |  | Water Density = | 62.4 | pcf
|  |  | Surcharge Load Equivalent Height = | 2
AASHTO LRFD Load Factors
Reference Tbl. 3.4.1-1 & 3.4.1-2
Limit State |  | EH | LL | WA
Service I |  | 1 | 1 | 1
Strength I |  | 1.5 | 1.75 | 1
Load Pressure Calculations | [14 empty] | y | x
Limit State |  | Depth Below Head (ft) | EH | LL | WA | [9 empty] | 0 | 0
Top of Wall |  | 0 | 0 | 105.4326 | 0 | psf | [8 empty] | 0 | 105.4326
Water Table |  | 16.187 | 853.3184 | 105.4326 | 0 | psf | [8 empty] | 11.987 | 737.3426
Bottom of Wall |  | 11.987 | 631.91 | 105.4326 | 0 | psf | [8 empty] | 11.987 | 0
PYWALL Unfiromly Distributed Load (LL Surcharge) Inputs
Location |  | Service I Min (lbs/in) | Strength I Max (lbs/in)
Top of Wall |  | 250 | 291.6667 | Note: Pywall uses a active earth modification factor, for service case it is 1 but for strength case it is 1.5 and it multiplies surcharge load by 1.5 by default so to get around this in strength case surchage load needs to be multiplied by 1.75/1.5.
Bottom of Wall |  | 250 | 291.6667
SOIL LAYER SETUP FOR PYWALL
No |  | Type |  | Depth at Top of the Layer | Depth at Bottom of Layer | Friction angle Φ | Unit Weight | Cohesive Strength | K (py) (pci) | E50 | Pressure coefficient
1 |  | Stiff Clay W/O Free Water (Reese) |  | 0.187 | 6.187 | 24 | 124 | 750 | 80 | 0.015 | 0.42173 | 0.42173
2 |  | Sand (Reese) |  | 6.187 | 11.987 | 28 | 110 | - | 25 | - | 0.42173 | 0.42173
3 |  | Sand (Reese) |  | 11.987 | 24.38 | 28 | 110 | - | 25 | -
5 |  | Stiff Clay With Free Water (Reese) |  | 24.38 | 33.687 | - | 126 | 1500 | 350 | 0.01
7 |  | Stiff Clay With Free Water (Reese) |  | 33.687 | 38.687 | - | 131 | 4500 | 1500 | 0.004
PYWALL results
SHEET PILE
[5 empty] | SECTION = | PZ 27
[5 empty] | Depth = | 36 | ft
[5 empty] | Service Level Deflection = | 3.215 | in | < OK | 3.5961 | in
[5 empty] | Strength Level Deflection = | 7.721 | in
[5 empty] | Max Strength I Moment Above Excavation Line = | 33.4917 | kip-ft | < OK | 169.875 | k-ft
[5 empty] | Max Strength I Moment Below Excavation Line = | 124.1667 | kip-ft | < OK | 169.875 | k-ft
[5 empty] | Max Strength I Shear = | 15.15 | kips | < OK | 87 | kips (LRFD Section 6.10.9.2)
STA I | X | DEFL. | SLOPE | MOMENT | SHEAR | SOIL_REACT | NET_FORCE/STA | EI |  |  | Depth (ft) | Deflection (in) | Moment (in-lbs) | Shear ( lbs) |  | Max Moment above |  |  | Max Shear
| FT | IN | RAD | LBS-IN | LBS | LBS/IN | LBS | LBS-IN**2 |  |  | 0 | 7.721 | -3.813e-07 | -1.765e-07 |  | 401900 | lb-in |  | 15150 |  | lbs
------ | ---- | ---- | ----- | ------ | ------ | --------- | --------- | --------- |  |  | 0.36 | 7.578 | -1.144e-06 | 57.44
0 | 0 | 7.721 | -0.03305 | -3.813e-07 | -1.765e-07 | 0 | -8.827e-08 | 8013000000 |  |  | 0.72 | 7.435 | 496.3 | 179.9
1 | 0.36 | 7.578 | -0.03305 | -1.144e-06 | 57.44 | 0 | 114.9 | 8013000000 |  |  | 1.08 | 7.292 | 1555 | 317.7 |  | Max Moment below
2 | 0.72 | 7.435 | -0.03305 | 496.3 | 179.9 | 0 | 130.1 | 8013000000 |  |  | 1.44 | 7.15 | 3241 | 470.7 |  | 1490000 | kip-in
3 | 1.08 | 7.292 | -0.03305 | 1555 | 317.7 | 0 | 145.4 | 8013000000 |  |  | 1.8 | 7.007 | 5622 | 639
4 | 1.44 | 7.15 | -0.03305 | 3241 | 470.7 | 0 | 160.6 | 8013000000 |  |  | 2.16 | 6.864 | 8762 | 822.5
5 | 1.8 | 7.007 | -0.03304 | 5622 | 639 | 0 | 175.9 | 8013000000 |  |  | 2.52 | 6.721 | 12730 | 1021
6 | 2.16 | 6.864 | -0.03304 | 8762 | 822.5 | 0 | 191.1 | 8013000000 |  |  | 2.88 | 6.579 | 17590 | 1235
7 | 2.52 | 6.721 | -0.03303 | 12730 | 1021 | 0 | 206.4 | 8013000000 |  |  | 3.24 | 6.436 | 23400 | 1464
8 | 2.88 | 6.579 | -0.03303 | 17590 | 1235 | 0 | 221.6 | 8013000000 |  |  | 3.6 | 6.293 | 30240 | 1709
9 | 3.24 | 6.436 | -0.03302 | 23400 | 1464 | 0 | 236.9 | 8013000000 |  |  | 3.96 | 6.151 | 38170 | 1969
10 | 3.6 | 6.293 | -0.033 | 30240 | 1709 | 0 | 252.1 | 8013000000 |  |  | 4.32 | 6.008 | 47250 | 2244
11 | 3.96 | 6.151 | -0.03298 | 38170 | 1969 | 0 | 267.4 | 8013000000 |  |  | 4.68 | 5.866 | 57550 | 2534
12 | 4.32 | 6.008 | -0.03296 | 47250 | 2244 | 0 | 282.6 | 8013000000 |  |  | 5.04 | 5.724 | 69140 | 2839
13 | 4.68 | 5.866 | -0.03293 | 57550 | 2534 | 0 | 297.9 | 8013000000 |  |  | 5.4 | 5.582 | 82080 | 3160
14 | 5.04 | 5.724 | -0.0329 | 69140 | 2839 | 0 | 313.1 | 8013000000 |  |  | 5.76 | 5.44 | 96450 | 3496
15 | 5.4 | 5.582 | -0.03286 | 82080 | 3160 | 0 | 328.4 | 8013000000 |  |  | 6.12 | 5.298 | 112300 | 3847
16 | 5.76 | 5.44 | -0.03281 | 96450 | 3496 | 0 | 343.6 | 8013000000 |  |  | 6.48 | 5.157 | 129700 | 4213
17 | 6.12 | 5.298 | -0.03275 | 112300 | 3847 | 0 | 358.9 | 8013000000 |  |  | 6.84 | 5.016 | 148700 | 4593
18 | 6.48 | 5.157 | -0.03269 | 129700 | 4213 | 0 | 372.7 | 8013000000 |  |  | 7.2 | 4.875 | 169400 | 4986
19 | 6.84 | 5.016 | -0.03261 | 148700 | 4593 | 0 | 386.3 | 8013000000 |  |  | 7.56 | 4.735 | 191800 | 5392
20 | 7.2 | 4.875 | -0.03253 | 169400 | 4986 | 0 | 399.8 | 8013000000 |  |  | 7.92 | 4.595 | 216000 | 5812
21 | 7.56 | 4.735 | -0.03243 | 191800 | 5392 | 0 | 413.3 | 8013000000 |  |  | 8.28 | 4.456 | 242000 | 6246
22 | 7.92 | 4.595 | -0.03232 | 216000 | 5812 | 0 | 426.8 | 8013000000 |  |  | 8.64 | 4.317 | 269900 | 6693
23 | 8.28 | 4.456 | -0.0322 | 242000 | 6246 | 0 | 440.4 | 8013000000 |  |  | 9 | 4.179 | 299800 | 7154
24 | 8.64 | 4.317 | -0.03206 | 269900 | 6693 | 0 | 453.9 | 8013000000 |  |  | 9.36 | 4.041 | 331700 | 7628
25 | 9 | 4.179 | -0.0319 | 299800 | 7154 | 0 | 467.4 | 8013000000 |  |  | 9.72 | 3.905 | 365700 | 8116
26 | 9.36 | 4.041 | -0.03173 | 331700 | 7628 | 0 | 480.9 | 8013000000 |  |  | 10.08 | 3.769 | 401900 | 8617
27 | 9.72 | 3.905 | -0.03155 | 365700 | 8116 | 0 | 494.5 | 8013000000 |  |  | 10.44 | 3.634 | 440200 | 9132
28 | 10.08 | 3.769 | -0.03134 | 401900 | 8617 | 0 | 508 | 8013000000 |  |  | 10.8 | 3.5 | 480800 | 9660
29 | 10.44 | 3.634 | -0.03111 | 440200 | 9132 | 0 | 521.5 | 8013000000 |  |  | 11.16 | 3.367 | 523600 | 10200
30 | 10.8 | 3.5 | -0.03086 | 480800 | 9660 | 0 | 535.1 | 8013000000 |  |  | 11.52 | 3.236 | 568900 | 10760
31 | 11.16 | 3.367 | -0.03059 | 523600 | 10200 | 0 | 548.6 | 8013000000 |  |  | 11.88 | 3.105 | 616600 | 11320
32 | 11.52 | 3.236 | -0.0303 | 568900 | 10760 | 0 | 562.1 | 8013000000 |  |  | 12.24 | 2.977 | 666700 | 11770
33 | 11.88 | 3.105 | -0.02998 | 616600 | 11320 | -0.7 | 572.6 | 8013000000 |  |  | 12.6 | 2.849 | 718200 | 11990
34 | 12.24 | 2.977 | -0.02963 | 666700 | 11770 | -43.17 | 310.2 | 8013000000 |  |  | 12.96 | 2.724 | 770300 | 12030
35 | 12.6 | 2.849 | -0.02926 | 718200 | 11990 | -84.93 | 129.7 | 8013000000 |  |  | 13.32 | 2.6 | 822100 | 11940
36 | 12.96 | 2.724 | -0.02886 | 770300 | 12030 | -126.7 | -50.69 | 8013000000 |  |  | 13.68 | 2.478 | 873400 | 11780
37 | 13.32 | 2.6 | -0.02843 | 822100 | 11940 | -143.4 | -123 | 8013000000 |  |  | 14.04 | 2.358 | 923900 | 11550
38 | 13.68 | 2.478 | -0.02797 | 873400 | 11780 | -160.2 | -195.3 | 8013000000 |  |  | 14.4 | 2.241 | 973200 | 11270
39 | 14.04 | 2.358 | -0.02749 | 923900 | 11550 | -176.9 | -267.6 | 8013000000 |  |  | 14.76 | 2.125 | 1021000 | 10970
40 | 14.4 | 2.241 | -0.02698 | 973200 | 11270 | -181.5 | -287.4 | 8013000000 |  |  | 15.12 | 2.012 | 1068000 | 10660
41 | 14.76 | 2.125 | -0.02644 | 1021000 | 10970 | -186.1 | -307.3 | 8013000000 |  |  | 15.48 | 1.902 | 1113000 | 10310
42 | 15.12 | 2.012 | -0.02587 | 1068000 | 10660 | -190.7 | -327.2 | 8013000000 |  |  | 15.84 | 1.794 | 1157000 | 9927
43 | 15.48 | 1.902 | -0.02529 | 1113000 | 10310 | -199.3 | -364.5 | 8013000000 |  |  | 16.2 | 1.689 | 1199000 | 9507
44 | 15.84 | 1.794 | -0.02467 | 1157000 | 9927 | -208 | -401.8 | 8013000000 |  |  | 16.56 | 1.586 | 1239000 | 9040
45 | 16.2 | 1.689 | -0.02404 | 1199000 | 9507 | -216.6 | -439.1 | 8013000000 |  |  | 16.92 | 1.487 | 1277000 | 8520
46 | 16.56 | 1.586 | -0.02338 | 1239000 | 9040 | -229.2 | -493.5 | 8013000000 |  |  | 17.28 | 1.39 | 1313000 | 7945
47 | 16.92 | 1.487 | -0.0227 | 1277000 | 8520 | -241.8 | -547.9 | 8013000000 |  |  | 17.64 | 1.296 | 1346000 | 7315
48 | 17.28 | 1.39 | -0.02201 | 1313000 | 7945 | -254.4 | -602.4 | 8013000000 |  |  | 18 | 1.206 | 1376000 | 6631
49 | 17.64 | 1.296 | -0.02129 | 1346000 | 7315 | -267 | -656.8 | 8013000000 |  |  | 18.36 | 1.119 | 1403000 | 5896
50 | 18 | 1.206 | -0.02055 | 1376000 | 6631 | -279.6 | -711.2 | 8013000000 |  |  | 18.72 | 1.035 | 1427000 | 5112
51 | 18.36 | 1.119 | -0.01981 | 1403000 | 5896 | -290.8 | -759.5 | 8013000000 |  |  | 19.08 | 0.9543 | 1447000 | 4280
52 | 18.72 | 1.035 | -0.01904 | 1427000 | 5112 | -302 | -807.8 | 8013000000 |  |  | 19.44 | 0.8771 | 1464000 | 3400
53 | 19.08 | 0.9543 | -0.01827 | 1447000 | 4280 | -313.1 | -856.2 | 8013000000 |  |  | 19.8 | 0.8032 | 1477000 | 2471
54 | 19.44 | 0.8771 | -0.01748 | 1464000 | 3400 | -324.3 | -904.5 | 8013000000 |  |  | 20.16 | 0.7329 | 1485000 | 1494
55 | 19.8 | 0.8032 | -0.01669 | 1477000 | 2471 | -335.5 | -952.8 | 8013000000 |  |  | 20.52 | 0.6659 | 1490000 | 468.8
56 | 20.16 | 0.7329 | -0.01589 | 1485000 | 1494 | -346.7 | -1001 | 8013000000 |  |  | 20.88 | 0.6025 | 1489000 | -604.6
57 | 20.52 | 0.6659 | -0.01509 | 1490000 | 468.8 | -357.9 | -1049 | 8013000000 |  |  | 21.24 | 0.5425 | 1484000 | -1726
58 | 20.88 | 0.6025 | -0.01429 | 1489000 | -604.6 | -369 | -1098 | 8013000000 |  |  | 21.6 | 0.486 | 1474000 | -2896
59 | 21.24 | 0.5425 | -0.01349 | 1484000 | -1726 | -380.2 | -1146 | 8013000000 |  |  | 21.96 | 0.4329 | 1459000 | -4089
60 | 21.6 | 0.486 | -0.01269 | 1474000 | -2896 | -391.4 | -1194 | 8013000000 |  |  | 22.32 | 0.3832 | 1439000 | -5226
61 | 21.96 | 0.4329 | -0.0119 | 1459000 | -4089 | -390.6 | -1191 | 8013000000 |  |  | 22.68 | 0.3368 | 1414000 | -6258
62 | 22.32 | 0.3832 | -0.01112 | 1439000 | -5226 | -366 | -1084 | 8013000000 |  |  | 23.04 | 0.2938 | 1385000 | -7188
63 | 22.68 | 0.3368 | -0.01035 | 1414000 | -6258 | -341.8 | -980 | 8013000000 |  |  | 23.4 | 0.254 | 1352000 | -8018
64 | 23.04 | 0.2938 | -0.009592 | 1385000 | -7188 | -318.4 | -878.7 | 8013000000 |  |  | 23.76 | 0.2173 | 1316000 | -8752
65 | 23.4 | 0.254 | -0.008854 | 1352000 | -8018 | -295.7 | -780.9 | 8013000000 |  |  | 24.12 | 0.1837 | 1276000 | -9394
66 | 23.76 | 0.2173 | -0.008134 | 1316000 | -8752 | -274.1 | -687.3 | 8013000000 |  |  | 24.48 | 0.153 | 1235000 | -10190
67 | 24.12 | 0.1837 | -0.007436 | 1276000 | -9394 | -253.3 | -597.4 | 8013000000 |  |  | 24.84 | 0.1253 | 1188000 | -11150
68 | 24.48 | 0.153 | -0.006759 | 1235000 | -10190 | -232 | -1002 | 8013000000 |  |  | 25.2 | 0.1003 | 1138000 | -12030
69 | 24.84 | 0.1253 | -0.006106 | 1188000 | -11150 | -211.6 | -914.1 | 8013000000 |  |  | 25.56 | 0.07796 | 1084000 | -12830
70 | 25.2 | 0.1003 | -0.005478 | 1138000 | -12030 | -194 | -838.1 | 8013000000 |  |  | 25.92 | 0.05814 | 1027000 | -13560
71 | 25.56 | 0.07796 | -0.004879 | 1084000 | -12830 | -177.8 | -767.9 | 8013000000 |  |  | 26.28 | 0.04072 | 967400 | -14200
72 | 25.92 | 0.05814 | -0.00431 | 1027000 | -13560 | -158.6 | -685.3 | 8013000000 |  |  | 26.64 | 0.02555 | 904700 | -14710
73 | 26.28 | 0.04072 | -0.003772 | 967400 | -14200 | -138.2 | -597.2 | 8013000000 |  |  | 27 | 0.01249 | 840300 | -15030
74 | 26.64 | 0.02555 | -0.003267 | 904700 | -14710 | -98.84 | -427 | 8013000000 |  |  | 27.36 | 0.001384 | 774800 | -15150
75 | 27 | 0.01249 | -0.002797 | 840300 | -15030 | -50.09 | -216.4 | 8013000000 |  |  | 27.72 | -0.007916 | 709300 | -15070
76 | 27.36 | 0.001384 | -0.002362 | 774800 | -15150 | -5.592 | -24.16 | 8013000000 |  |  | 28.08 | -0.01556 | 644700 | -14780
77 | 27.72 | -0.007916 | -0.001962 | 709300 | -15070 | 44.97 | 194.3 | 8013000000 |  |  | 28.44 | -0.02171 | 581600 | -14320
78 | 28.08 | -0.01556 | -0.001597 | 644700 | -14780 | 88.86 | 383.9 | 8013000000 |  |  | 28.8 | -0.0265 | 521000 | -13720
79 | 28.44 | -0.02171 | -0.001266 | 581600 | -14320 | 124.6 | 538.1 | 8013000000 |  |  | 29.16 | -0.03008 | 463100 | -13010
80 | 28.8 | -0.0265 | -0.0009687 | 521000 | -13720 | 152.8 | 660.1 | 8013000000 |  |  | 29.52 | -0.03258 | 408500 | -12230
81 | 29.16 | -0.03008 | -0.0007035 | 463100 | -13010 | 174.3 | 752.9 | 8013000000 |  |  | 29.88 | -0.03413 | 357500 | -11390
82 | 29.52 | -0.03258 | -0.0004685 | 408500 | -12230 | 189.7 | 819.4 | 8013000000 |  |  | 30.24 | -0.03484 | 310200 | -10510
83 | 29.88 | -0.03413 | -0.000262 | 357500 | -11390 | 199.7 | 862.5 | 8013000000 |  |  | 30.6 | -0.03484 | 266700 | -9625
84 | 30.24 | -0.03484 | -8.202e-05 | 310200 | -10510 | 204.8 | 884.8 | 8013000000 |  |  | 30.96 | -0.03421 | 227000 | -8742
85 | 30.6 | -0.03484 | 7.348e-05 | 266700 | -9625 | 205.8 | 888.9 | 8013000000 |  |  | 31.32 | -0.03305 | 191100 | -7877
86 | 30.96 | -0.03421 | 0.0002066 | 227000 | -8742 | 203 | 877.1 | 8013000000 |  |  | 31.68 | -0.03145 | 158900 | -7045
87 | 31.32 | -0.03305 | 0.0003193 | 191100 | -7877 | 197.1 | 851.4 | 8013000000 |  |  | 32.04 | -0.02948 | 130300 | -6254
88 | 31.68 | -0.03145 | 0.0004136 | 158900 | -7045 | 188.4 | 814 | 8013000000 |  |  | 32.4 | -0.0272 | 104900 | -5516
89 | 32.04 | -0.02948 | 0.0004916 | 130300 | -6254 | 177.4 | 766.5 | 8013000000 |  |  | 32.76 | -0.02468 | 82610 | -4835
90 | 32.4 | -0.0272 | 0.000555 | 104900 | -5516 | 164.6 | 711.2 | 8013000000 |  |  | 33.12 | -0.02197 | 63120 | -4221
91 | 32.76 | -0.02468 | 0.0006055 | 82610 | -4835 | 150.2 | 648.8 | 8013000000 |  |  | 33.48 | -0.01911 | 46150 | -3676
92 | 33.12 | -0.02197 | 0.0006448 | 63120 | -4221 | 134.4 | 580.7 | 8013000000 |  |  | 33.84 | -0.01614 | 31360 | -3207
93 | 33.48 | -0.01911 | 0.0006743 | 46150 | -3676 | 117.6 | 507.8 | 8013000000 |  |  | 34.2 | -0.0131 | 18440 | -2815
94 | 33.84 | -0.01614 | 0.0006952 | 31360 | -3207 | 99.83 | 431.3 | 8013000000 |  |  | 34.56 | -0.01002 | 7035 | -1994
95 | 34.2 | -0.0131 | 0.0007086 | 18440 | -2815 | 81.47 | 351.9 | 8013000000 |  |  | 34.92 | -0.006923 | 1208 | -901.6
96 | 34.56 | -0.01002 | 0.0007155 | 7035 | -1994 | 298.7 | 1290 | 8013000000 |  |  | 35.28 | -0.003821 | -754.6 | -206.8
97 | 34.92 | -0.006923 | 0.0007177 | 1208 | -901.6 | 207.1 | 894.7 | 8013000000 |  |  | 35.64 | -0.0007209 | -579.3 | 87.34
98 | 35.28 | -0.003821 | 0.0007178 | -754.6 | -206.8 | 114.5 | 494.8 | 8013000000 |  |  | 36 | 0.002378 | -3.724e-10 | 67.05
99 | 35.64 | -0.0007209 | 0.0007175 | -579.3 | 87.34 | 21.65 | 93.54 | 8013000000
100 | 36 | 0.002378 | 0.0007173 | -3.724e-10 | 67.05 | -31.04 | -134.1 | 8013000000
Note on E18: tadams: Enter these into the soil properties in PYWall
Note on E21: tadams: Traffic is more than 0.5x the height of the wall away from the wall.
Note on A65: aibrahimkhail: results from Pywall

## Wall info_AutoTable
TEMPORARY SHORING DATA TABLE
WALL NUMBER | REFERENCE ALIGNMENT | BEGIN STATION | BEGIN OFFSET (FT) | BEGIN TOP OF WALL EL | END STATION | END OFFSET (FT) | END TOP OF WALL EL | LENGTH (FT)
1 | CL BRIDGE ST | 201+08.57 | 2.17 RT | 943.477 | 201+43.86 | 0.39 RT | 943.606 | 35.64
2 | CL WATER ALLEY | 0+17.57 | 2.50 RT | 942.81 | 0+60.56 | 2.23 RT | 938.956 | 43
3 | CL BRIDGE ST | 202+14.46 | 0.39 RT | 939.987 | 202.52.98 | 0.68 RT | 939.06 | 38.55

## Design data_Autotable
TEMPORARY SHORING DATA TABLE (CONT)
WALL NUMBER | MAX RETAINED HEIGHT, H (FT) | STEEL GRADE (KSI) | MIN SECTION MODULUS (IN3/FT) | MIN MOMENT OF INERTIA (IN4/FT) | MIN EMBEDMENT DEPTH, D (FT)
1 | 12.197 | 50 | 60.7 | 490.85 | 27.903
2 | 11.53 | 50 | 60.7 | 490.85 | 28.47
3 | 11.987 | 50 | 30.2 | 184.2 | 24.013

## SCRATCH
[6 empty] | degrees | radians
0.46947 |  |  |  | internal friction | Φ | 28 | 0.48869
0.46947 |  |  |  | backslope | ß | 0 | 0
1 |  |  |  | friction | delta | 0 | 0
1 |  |  |  | angle of … | 𝜃 or alpha | 90 | 1.5708
= (1+ | 0.46947 | = | 2.1593
0.88295
1
1
= | 0.36103

## Wall A - Section 2 OLD (hidden)
[6 empty] | Made by: | RJE | Date: | 2002-03-08 | Job No: | 20110903
[6 empty] | Checked by: |  | Date: |  | Sheet No: | 1
[6 empty] | Project: | HAM-75-7.85 |  | PID: | 77889
[6 empty] | Subject: | Temporary Wall A - Section 2
Temporary Wall A - Section 2
Soil Properties Based off of Borring B-162
Design Height Based on Pile #9
Top of Wall Elevation = | #REF!
Bottom of Wall Elevation = | 515.27 | ft
Water Table Elevation = | 511.7
H (design)= | #REF! | ft
Su = | 1000 | psf | (Conservative)
Gamma = | 115 | pcf
Piling Spacing S = | 8.5 | ft
ka = | 0.47 | Boring B-162 indicates upper layers are soft to medium stiff clay
Water Density = | 62.4 | pcf
Surcharge Load Equivalent Height = | 0 | Traffic is greater than .5*H from back of wall
p multiplier inputted into L-Pile | 0.76139 | BDM 305.1.2
AASHTO LRFD Load Factors
Reference Tbl. 3.4.1-1 & 3.4.1-2
Limit State |  | EH | LL | WA
Service I |  | 1 | 1 | 1
Strength I |  | 1.5 | 1.75 | 1
Load Pressure Calculations
Limit State |  | EH | LL | WA
Top of Wall | 0.1 | #REF! | 0 | #REF! | psf
Water Table | #REF! | #REF! | 0 | #REF! | psf
Bottom of Wall | #REF! | #REF! | 0 | #REF! | psf
Lpile Distributed Load Inputs
Location | Depth Below Head (ft) | Service I Min (lbs/in) | Strength I Max (lbs/in)
Top of Wall | 0.1 | #REF! | #REF!
Water Table | #REF! | #REF! | #REF!
Bottom of Wall | #REF! | #REF! | #REF!
Per L-Pile Results Below, Depth of 3'-0" Diameter Drilled Shaft = | 35 | ft
Diameter of Drilled Shaft = | 3 | ft
Soldier Pile Section = | W24x176 |  |  | Allowable/Capacity
Max Service Level Deflection = | 3.22 | in | #REF! | #REF!
Max Strength I Moment Above Drilled Shaft = | 382.9221 | kip-ft | < OK | 1748.45 | k-ft
Max Strength I Moment Below Drilled Shaft = | 763.2975 | kip-ft | < OK | 1916.25 | k-ft
Max Strength I Shear = | 76.426 | kips | < OK | 548.1 | kips (LRFD Section 6.10.9.2)
Note on B10: REly: Average Top of Ground elevation triburary to Pile #9.
Note on B16: rely: Average between the two adjacent spans of 12' and 5'.
Note on B21: rely: Conservatively set this to the 5' spacing p multiplier on the one side of the pile.
Note on B41: tadams: do we need to be this deep?
Note on B43: tadams: By upsizing to the W27-146 we have less than 3" clear from the edge of shaft to tip of pile, which is less than what is typically desired for steel clearance in drilled shafts. Lets switch this out to a 24x176.

## Walls A - Section 3_Old (hidden)
[6 empty] | Made by: | RJE | Date: | 2023-03-08 | Job No: | 20110903
[6 empty] | Checked by: |  | Date: |  | Sheet No: | 1
[6 empty] | Project: | HAM-75-7.85 |  | PID: | 77889
[6 empty] | Subject: | Temporary Wall A - Section 3
Temporary Wall A - Section 3
Soil Properties Based off of Borring B-162
Design Height Based on Pile #11
Top of Wall Elevation = | 527.33
Bottom of Wall Elevation = | 515.27 | ft
Water Table Elevation = | 511.7
H (design)= | 12.06 | ft
Su = | 1000 | psf | (Conservative)
Gamma = | 115 | pcf
Piling Spacing S = | 5 | ft
ka = | 0.47 | Boring B-162 indicates upper layers are soft to medium stiff clay
Water Density = | 62.4 | pcf
Surcharge Load Equivalent Height = | 0 | Traffic is greater than .5*H from back of wall
p multiplier inputted into L-Pile | 0.81008 | BDM 305.1.2
AASHTO LRFD Load Factors
Reference Tbl. 3.4.1-1 & 3.4.1-2
Limit State |  | EH | LL | WA
Service I |  | 1 | 1 | 1
Strength I |  | 1.5 | 1.75 | 1
Load Pressure Calculations
Limit State |  | EH | LL | WA
Top of Wall | 0.1 | 5.405 | 0 | 0 | psf
Water Table | 15.63 | 844.8015 | 0 | 0 | psf
Bottom of Wall | 12.06 | 651.843 | 0 | 0 | psf
Lpile Distributed Load Inputs
Location | Depth Below Head (ft) | Service I Min (lbs/in) | Strength I Max (lbs/in)
Top of Wall | 0.1 | 2.2521 | 3.3781
Water Table | 15.63 | 352.0006 | 528.0009
Bottom of Wall | 12.06 | 271.6013 | 407.4019
Per L-Pile Results Below, Depth of 3'-0" Diameter Drilled Shaft = | 25 | ft
Diameter of Drilled Shaft = | 2.5 | ft
Soldier Pile Section = | W21x44 |  |  | Allowable/Capacity
Max Service Level Deflection = | 2.8818 | in | < OK | 2.8944
Max Strength I Moment Above Drilled Shaft = | 123.5318 | kip-ft | < OK | 229.943 | k-ft
Max Strength I Moment Below Drilled Shaft = | 303.5763 | kip-ft | < OK | 357.75 | k-ft
Max Strength I Shear = | 29.478 | kips | < OK | 210.105 | kips (LRFD Section 6.10.9.2)
Note on B10: REly: Conservatively take existing top of concrete slope protection at face of abutment (elevation per survey points and record plan info)
Note on E45: tadams: just pulled this from enercalc
Note on E46: tadams: just pulled this from Enercalc