## DECORATIVE
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
[8 empty] | Designed By |  | MDH
[8 empty] | Checked By |  | STB
County-Route-Section: |  | LAK-615-4.03; PID: 98564 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 120/240 | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 |  | Luminaire Wattage: |  | 242 |  | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | [9 empty] | 1/0 | 0.12
[11 empty] | 2/0 | 0.1
[11 empty] | 4/0 | 0.079
AUTOMATICALLY CALCULATED
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point |  | ENTER DATA
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
CIRCUIT A | [9 empty] | CIRCUIT A
L-4 | L-2 | 300 | 1.3108 | 1.3108 | 393.25 | 4 | 0.24382 | 4.2269 | 1.7612 | L-2
L-2 | PB-5 | 335 | 1.3108 | 2.6217 | 878.2583 | 4 | 0.54452 | 3.9831 | 1.6596 | PB-5
PB-5 | PB-4 | 68 | 0 | 2.6217 | 178.2733 | 4 | 0.11053 | 3.4386 | 1.4328 | PB-4
L-5 | L-3 | 310 | 1.3108 | 1.3108 | 406.3583 | 4 | 0.25194 | 4.5268 | 1.8862 | L-3
L-3 | L-1 | 290 | 1.3108 | 2.6217 | 760.2833 | 4 | 0.47138 | 4.2749 | 1.7812 | L-1
L-1 | PB-4 | 195 | 1.3108 | 3.9325 | 766.8375 | 4 | 0.47544 | 3.8035 | 1.5848 | PB-4
PB-4 | PB-3 | 225 | 0 | 6.5542 | 1474.6875 | 4 | 0.91431 | 3.3281 | 1.3867 | PB-3
PB-3 | PB-2 | 260 | 0 | 6.5542 | 1704.0833 | 4 | 1.0565 | 2.4138 | 1.0057 | PB-2
PB-2 | PB-1 | 286 | 0 | 6.5542 | 1874.4917 | 4 | 1.1622 | 1.3572 | 0.56552 | PB-1
PB-1 | PS-C | 48 | 0 | 6.5542 | 314.6 | 4 | 0.19505 | 0.19505 | 0.081272 | PS-C

## AEL
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
[8 empty] | Designed By |  | MDH
[8 empty] | Checked By |  | STB
County-Route-Section: |  | LAK-615-4.03; PID: 98564 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 120/240 | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 |  | Luminaire Wattage: |  | 190 |  | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | [9 empty] | 1/0 | 0.12
[11 empty] | 2/0 | 0.1
[11 empty] | 4/0 | 0.079
AUTOMATICALLY CALCULATED
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point |  | ENTER DATA
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
CIRCUIT A | [9 empty] | CIRCUIT A
L-4 | L-2 | 300 | 1.0292 | 1.0292 | 308.75 | 4 | 0.19142 | 3.3187 | 1.3828 | L-2
L-2 | PB-5 | 335 | 1.0292 | 2.0583 | 689.5417 | 4 | 0.42752 | 3.1272 | 1.303 | PB-5
PB-5 | PB-4 | 68 | 0 | 2.0583 | 139.9667 | 4 | 0.086779 | 2.6997 | 1.1249 | PB-4
L-5 | L-3 | 310 | 1.0292 | 1.0292 | 319.0417 | 4 | 0.19781 | 3.5541 | 1.4809 | L-3
L-3 | L-1 | 290 | 1.0292 | 2.0583 | 596.9167 | 4 | 0.37009 | 3.3563 | 1.3985 | L-1
L-1 | PB-4 | 195 | 1.0292 | 3.0875 | 602.0625 | 4 | 0.37328 | 2.9862 | 1.2443 | PB-4
PB-4 | PB-3 | 225 | 0 | 5.1458 | 1157.8125 | 4 | 0.71784 | 2.613 | 1.0887 | PB-3
PB-3 | PB-2 | 260 | 0 | 5.1458 | 1337.9167 | 4 | 0.82951 | 1.8951 | 0.78963 | PB-2
PB-2 | PB-1 | 286 | 0 | 5.1458 | 1471.7083 | 4 | 0.91246 | 1.0656 | 0.444 | PB-1
PB-1 | PS-C | 48 | 0 | 5.1458 | 247 | 4 | 0.15314 | 0.15314 | 0.063808 | PS-C

## COOPER VERDEON
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
[8 empty] | Designed By |  | MDH
[8 empty] | Checked By |  | STB
County-Route-Section: |  | LAK-615-4.03; PID: 98564 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 120/240 | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 |  | Luminaire Wattage: |  | 182 |  | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | [9 empty] | 1/0 | 0.12
[11 empty] | 2/0 | 0.1
[11 empty] | 4/0 | 0.079
AUTOMATICALLY CALCULATED
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point |  | ENTER DATA
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
CIRCUIT A | [9 empty] | CIRCUIT A
L-4 | L-2 | 298 | 0.98583 | 0.98583 | 293.7783 | 4 | 0.18214 | 3.1802 | 1.3251 | L-2
L-2 | PB-5 | 337 | 0.98583 | 1.9717 | 664.4517 | 4 | 0.41196 | 2.998 | 1.2492 | PB-5
PB-5 | PB-4 | 68 | 0 | 1.9717 | 134.0733 | 4 | 0.083125 | 2.5861 | 1.0775 | PB-4
L-5 | L-3 | 310 | 0.98583 | 0.98583 | 305.6083 | 4 | 0.18948 | 3.4045 | 1.4185 | L-3
L-3 | L-1 | 290 | 0.98583 | 1.9717 | 571.7833 | 4 | 0.35451 | 3.215 | 1.3396 | L-1
L-1 | PB-4 | 195 | 0.98583 | 2.9575 | 576.7125 | 4 | 0.35756 | 2.8605 | 1.1919 | PB-4
PB-4 | PB-3 | 225 | 0 | 4.9292 | 1109.0625 | 4 | 0.68762 | 2.5029 | 1.0429 | PB-3
PB-3 | PB-2 | 260 | 0 | 4.9292 | 1281.5833 | 4 | 0.79458 | 1.8153 | 0.75638 | PB-2
PB-2 | PB-1 | 286 | 0 | 4.9292 | 1409.7417 | 4 | 0.87404 | 1.0207 | 0.4253 | PB-1
PB-1 | PS-C | 48 | 0 | 4.9292 | 236.6 | 4 | 0.14669 | 0.14669 | 0.061122 | PS-C

## GE
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
[8 empty] | Designed By |  | MDH
[8 empty] | Checked By |  | STB
County-Route-Section: |  | LAK-615-4.03; PID: 98564 |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 120/240 | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: | [10 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 |  | Luminaire Wattage: |  | 285 |  | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | [9 empty] | 1/0 | 0.12
[11 empty] | 2/0 | 0.1
[11 empty] | 4/0 | 0.079
AUTOMATICALLY CALCULATED
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point |  | ENTER DATA
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
CIRCUIT A | [9 empty] | CIRCUIT A
L-4 | L-2 | 300 | 1.5437 | 1.5437 | 463.125 | 4 | 0.28714 | 4.978 | 2.0742 | L-2
L-2 | PB-5 | 335 | 1.5437 | 3.0875 | 1034.3125 | 4 | 0.64127 | 4.6909 | 1.9545 | PB-5
PB-5 | PB-4 | 68 | 0 | 3.0875 | 209.95 | 4 | 0.13017 | 4.0496 | 1.6873 | PB-4
L-5 | L-3 | 310 | 1.5437 | 1.5437 | 478.5625 | 4 | 0.29671 | 5.3312 | 2.2213 | L-3
L-3 | L-1 | 290 | 1.5437 | 3.0875 | 895.375 | 4 | 0.55513 | 5.0345 | 2.0977 | L-1
L-1 | PB-4 | 195 | 1.5437 | 4.6312 | 903.0937 | 4 | 0.55992 | 4.4793 | 1.8664 | PB-4
PB-4 | PB-3 | 225 | 0 | 7.7188 | 1736.7188 | 4 | 1.0768 | 3.9194 | 1.6331 | PB-3
PB-3 | PB-2 | 260 | 0 | 7.7188 | 2006.875 | 4 | 1.2443 | 2.8427 | 1.1844 | PB-2
PB-2 | PB-1 | 286 | 0 | 7.7188 | 2207.5625 | 4 | 1.3687 | 1.5984 | 0.666 | PB-1
PB-1 | PS-C | 48 | 0 | 7.7188 | 370.5 | 4 | 0.22971 | 0.22971 | 0.095712 | PS-C