## Circuit A
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | LCC-A | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  |  | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Circuit: 'A'
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
AA-6 | AA-5 | 141 | 2.2 | 2.2 | 310.2 | 4 | 0.19232 | 3.6105 | 1.5044 | AA-6
AA-5 | AA-4 | 143 | 2.2 | 4.4 | 629.2 | 4 | 0.3901 | 3.4182 | 1.4242 | AA-5
AA-4 | AA-3 | 143 | 2.2 | 6.6 | 943.8 | 4 | 0.58516 | 3.0281 | 1.2617 | AA-4
AA-3 | AA-2 | 221 | 2.2 | 8.8 | 1944.8 | 4 | 1.2058 | 2.4429 | 1.0179 | AA-3
AA-2 | AA-1 | 155 | 2.2 | 11 | 1705 | 4 | 1.0571 | 1.2371 | 0.51548 | AA-2
AA-1 | LCC-A | 22 | 2.2 | 13.2 | 290.4 | 4 | 0.18005 | 0.18005 | 0.07502 | AA-1
120
240
480

## Circuit B
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | LCC-A | Circuit: | B | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  |  | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Circuit: 'B'
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
AB-5 | AB-4 | 131 | 2.2 | 2.2 | 288.2 | 4 | 0.17868 | 3.8547 | 1.6061 | AB-5
AB-4 | AB-3 | 130 | 2.2 | 4.4 | 572 | 4 | 0.35464 | 3.676 | 1.5317 | AB-4
AB-3 | AB-2 | 129 | 2.2 | 6.6 | 851.4 | 4 | 0.52787 | 3.3213 | 1.3839 | AB-3
AB-2 | AB-1 | 147 | 2.2 | 8.8 | 1293.6 | 4 | 0.80203 | 2.7935 | 1.1639 | AB-2
AB-1 | LCC-A | 292 | 2.2 | 11 | 3212 | 4 | 1.9914 | 1.9914 | 0.82977 | AB-1
120
240
480

## Circuit C
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: | [5 empty] | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | LCC-A | Circuit: | C | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 240 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  |  | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000 |  | Circuit: 'C'
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
AC-4 | AC-3 | 207 | 1.4 | 1.4 | 289.8 | 4 | 0.17968 | 1.6058 | 0.66908 | AC-4
AC-3 | AC-2 | 217 | 1.4 | 2.8 | 607.6 | 4 | 0.37671 | 1.4261 | 0.59422 | AC-3
AC-2 | AC-1 | 179 | 1.4 | 4.2 | 751.8 | 4 | 0.46612 | 1.0494 | 0.43725 | AC-2
AC-1 | LCC-A | 168 | 1.4 | 5.6 | 940.8 | 4 | 0.5833 | 0.5833 | 0.24304 | AC-1
240
480