## Circuit TN
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | SUM-77 NB Vacant Rest Area TP |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | GR | Circuit: | 1 | [6 empty] | 10 | 1.2
Supply Voltage: |  | 480 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 4 | AWG. | 0.31 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 480 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  | Circuit: 'TE' | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
GR-17 | GR-16 | 470 | 0.17 | 0.17 | 79.9 | 4 | 0.049538 | 9.6663 | 2.0138 | GR-17
GR-16 | GR-15 | 208 | 0.17 | 0.34 | 70.72 | 4 | 0.043846 | 9.6168 | 2.0035 | GR-16
GR-15 | PB-2 | 139 | 0.17 | 0.51 | 70.89 | 4 | 0.043952 | 9.5729 | 1.9944 | GR-15
GR-14 | PB-2 | 29 | 0.17 | 0.17 | 4.93 | 4 | 0.0030566 | 9.532 | 1.9858 | GR-14
PB-2 | GR-13 | 308 | 0 | 0.68 | 209.44 | 4 | 0.12985 | 9.529 | 1.9852 | PB-2
GR-13 | GR-12 | 237 | 1.38 | 2.06 | 488.22 | 4 | 0.3027 | 9.3991 | 1.9581 | GR-13
GR-12 | GR-11 | 160 | 1.38 | 3.44 | 550.4 | 4 | 0.34125 | 9.0964 | 1.8951 | GR-12
GR-11 | PB-5 | 112 | 0.17 | 3.61 | 404.32 | 4 | 0.25068 | 8.7552 | 1.824 | GR-11
GR-10 | GR-9 | 238 | 1.38 | 1.38 | 328.44 | 4 | 0.20363 | 9.3361 | 1.945 | GR-10
GR-9 | PB-5 | 367 | 1.38 | 2.76 | 1012.92 | 4 | 0.62801 | 9.1325 | 1.9026 | GR-9
PB-5 | GR-8 | 66 | 0 | 6.37 | 420.42 | 4 | 0.26066 | 8.5045 | 1.7718 | PB-5
GR-8 | GR-7 | 235 | 0.17 | 6.54 | 1536.9 | 4 | 0.95288 | 8.2438 | 1.7175 | GR-8
GR-7 | GR-6 | 239 | 0.17 | 6.71 | 1603.69 | 4 | 0.99429 | 7.2909 | 1.5189 | GR-7
GR-6 | GR-5 | 240 | 0.17 | 6.88 | 1651.2 | 4 | 1.0237 | 6.2967 | 1.3118 | GR-6
GR-5 | GR-4 | 240 | 0.17 | 7.05 | 1692 | 4 | 1.049 | 5.2729 | 1.0985 | GR-5
GR-4 | GR-3 | 240 | 0.17 | 7.22 | 1732.8 | 4 | 1.0743 | 4.2239 | 0.87997 | GR-4
GR-3 | GR-2 | 240 | 0.17 | 7.39 | 1773.6 | 4 | 1.0996 | 3.1495 | 0.65615 | GR-3
GR-2 | GR-1 | 240 | 0.17 | 7.56 | 1814.4 | 4 | 1.1249 | 2.0499 | 0.42706 | GR-2
GR-1 | CC-'GR' | 193 | 0.17 | 7.73 | 1491.89 | 4 | 0.92497 | 0.92497 | 0.1927 | GR-1
120
240
480