## Circuit A
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | TUS-GNADENHUTTEN |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 120 | Circuit: | A | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 8 | AWG. | 0.78 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 120 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  |  | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
CC | PB-1 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | CC
PB-1 | LP-1 | 41 | 0.28 | 0.28 | 11.48 | 8 | 0.017909 | 0.017909 | 0.014924 | PB-1
PB-1 | LP-2 | 125 | 0.28 | 0.56 | 70 | 8 | 0.1092 | 0.12711 | 0.10592 | PB-1
LP-2 | PB-3 | 62 | 0 | 0.56 | 34.72 | 8 | 0.054163 | 0.18127 | 0.15106 | LP-2
PB-3 | LP-3 | 65 | 0.28 | 0.84 | 54.6 | 8 | 0.085176 | 0.26645 | 0.22204 | PB-3
PB-3 | DL-1 | 130 | 0.56 | 1.4 | 182 | 8 | 0.28392 | 0.55037 | 0.45864 | PB-3
DL-1 | PB-5 | 77 | 0 | 1.4 | 107.8 | 8 | 0.16817 | 0.71854 | 0.59878 | DL-1
PB-5 | DL-2 | 90 | 0.56 | 1.96 | 176.4 | 8 | 0.27518 | 0.99372 | 0.8281 | PB-5
PB-5 | LP-4 | 112 | 0.28 | 2.24 | 250.88 | 8 | 0.39137 | 1.3851 | 1.1542 | PB-5
LP-4 | PB-7 | 100 | 0 | 2.24 | 224 | 8 | 0.34944 | 1.7345 | 1.4454 | LP-4
PB-7 | LP-5 | 41 | 0.28 | 2.52 | 103.32 | 8 | 0.16118 | 1.8957 | 1.5798 | PB-7
PB-7 | LP-6 | 98 | 0.28 | 2.8 | 274.4 | 8 | 0.42806 | 2.3238 | 1.9365 | PB-7

## Circuit B
VOLTAGE DROP CALCULATIONS | [10 empty] | 14 | 3.1
County-Route-Section: |  | TUS-GNADENHUTTEN |  |  |  | No. of Wires for Calculation Purposes: |  |  |  | 2 | 12 | 2
Power Service: |  | 120 | Circuit: | B | [6 empty] | 10 | 1.2
Supply Voltage: |  | 120 | [8 empty] | 8 | 0.78
Wire Resistance Used: |  | No. | 8 | AWG. | 0.78 | [5 empty] | 6 | 0.49
|  | No. |  | AWG. | [6 empty] | 4 | 0.31
[11 empty] | 2 | 0.19
Voltage: | 120 | Wire Factor Used (Two - No. 10 AWG Wires): |  |  |  |  | 2.4 | ohms/mft/1000 |  |  | 1/0 | 0.12
|  | Wire Factor Used (Two - No. 8 AWG Wires): |  |  |  |  | 1.56 | ohms/mft/1000 |  |  | 2/0 | 0.1
|  | Wire Factor Used (Two - No. 6 AWG Wires): |  |  |  |  | 0.98 | ohms/mft/1000 |  |  | 4/0 | 0.079
|  | Wire Factor Used (Two - No. 4 AWG Wires): |  |  |  |  | 0.62 | ohms/mft/1000
Section |  |  | Amperes |  | Ampere- Feet | AWG | Voltage Drop |  | % Drop | At Point
From | To | Design Feet | At Point | Accum. |  |  | In Section | Accum.
CC | PB-5 | 396 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | CC
PB-5 | LP-9 | 72 | 0.28 | 0.28 | 20.16 | 8 | 0.03145 | 0.03145 | 0.026208 | PB-5
LP-9 | PB-10 | 70 | 0 | 0.28 | 19.6 | 8 | 0.030576 | 0.062026 | 0.051688 | LP-9
PB-10 | LP-8 | 77 | 0.28 | 0.56 | 43.12 | 8 | 0.067267 | 0.12929 | 0.10774 | PB-10
PB-10 | LP-7 | 129 | 0.28 | 0.84 | 108.36 | 8 | 0.16904 | 0.29833 | 0.24861 | PB-10
PB-5 | PB-9 | 112 | 0 | 0.84 | 94.08 | 8 | 0.14676 | 0.4451 | 0.37092 | PB-5
PB-9 | LP-10 | 81 | 0.28 | 1.12 | 90.72 | 8 | 0.14152 | 0.58662 | 0.48885 | PB-9
PB-9 | LP-11 | 104 | 0.28 | 1.4 | 145.6 | 8 | 0.22714 | 0.81376 | 0.67813 | PB-9
LP-11 | PB-8 | 76 | 0 | 1.4 | 106.4 | 8 | 0.16598 | 0.97974 | 0.81645 | LP-11
PB-8 | LP-12 | 80 | 0.28 | 1.68 | 134.4 | 8 | 0.20966 | 1.1894 | 0.99117 | PB-8
PB-8 | LP-13 | 101 | 0.28 | 1.96 | 197.96 | 8 | 0.30882 | 1.4982 | 1.2485 | PB-8